## MySQL
ColumnName | DataLabel | DataType | Description
V0 | DATETIME | DATETIME | Time stamp in DATETIME format
V1 | POWER_P_DG_TOTAL | FLOAT | Total genset active power [kW]
V2 | POWER_Q_DG_TOTAL | FLOAT | Total genset reactive power [kVAr]
V3 | POWER_P_PV_TOTAL | FLOAT | Total PV active power [kW]
V4 | POWER_Q_PV_TOTAL | FLOAT | Total PV reactive power [kVAr]
V5 | POWER_P_MAINS_TOTAL | FLOAT | Total Mains active power [kW]
V6 | POWER_Q_MAINS_TOTAL | FLOAT | Total Mains reactive power [kVAr]
V7 | POWER_P_LOAD_TOTAL | FLOAT | Total active Load [kW]
V8 | POWER_Q_LOAD_TOTAL | FLOAT | Total reactive Load [kVAr]
V9 | PV_P_GENERATING_CAPACITY | FLOAT | Total PV generating capacity active power [kW]
V10 | PV_Q_GENERATING_CAPACITY | FLOAT | Total PV generating capacity reactive power [kVAr]
V11 | PV_P_POWER_TARGET | FLOAT | PV target reference active power [kW]
V12 | PV_Q_POWER_TARGET | FLOAT | PV target reference reactive power [kVAr]
V13 | PV_P_POWER_REFERENCE | FLOAT | PV actual reference active power [kW]
V14 | PV_Q_POWER_REFERENCE | FLOAT | PV actual reference reactive power [kVAr]
V15 | DG_P_GENERATING_CAPACITY | FLOAT | Total genset generating capacity active power [kW]
V16 | DG_P_LOADING_PCT | FLOAT | Genset active power loading [%]
V17 | DG_P_MIN_LOADING_KW | FLOAT | Minimum genset load [kW]
V18 | MAINS_P_GENERATING_CAPACITY | FLOAT | Total Mains generating capacity active power [kW]
V19 | SENSOR_POA | FLOAT | POA irradiance [W/m2]
V20 | SENSOR_BOM | FLOAT | Back of module temperature [C]
V21 | ANY_GB_POS_ON | BOOLEAN | Any genset breaker closed
V22 | ANY_MB_POS_ON | BOOLEAN | Any Mains breaker closed
V23 | CURTAILMENT | BOOLEAN | Curtailment active
V24 | PV_STARTED | BOOLEAN | PV started
V25 | STATUSTEXT01 | CHAR(80) | ECweb status text 1
V26 | STATUSTEXT02 | CHAR(80) | ECweb status text 2
V27 | STATUSTEXT03 | CHAR(80) | ECweb status text 3
V28 | DG_KWH_TOTAL | FLOAT | Total genset energy production [kWh]
V29 | DG_KWH_YEAR | FLOAT | Genset energy production current year [kWh]
V30 | DG_KWH_MONTH | FLOAT | Genset energy production current month [kWh]
V31 | DG_KWH_DAY | FLOAT | Genset energy production current day [kWh]
V32 | PV_KWH_TOTAL | FLOAT | Total PV energy production [kWh]
V33 | PV_KWH_YEAR | FLOAT | PV energy production current year [kWh]
V34 | PV_KWH_MONTH | FLOAT | PV energy production current month [kWh]
V35 | PV_KWH_DAY | FLOAT | PV energy production current day [kWh]
V36 | PV_KWH_CUR_TOTAL | FLOAT | Total PV energy production curtailed [kWh]
V37 | PV_KWH_CUR_YEAR | FLOAT | PV energy production curtailed current year [kWh]
V38 | PV_KWH_CUR_MONTH | FLOAT | PV energy production curtailed current month [kWh]
V39 | PV_KWH_CUR_DAY | FLOAT | PV energy production curtailed current day [kWh]
V40 | MAINS_KWH_TOTAL | FLOAT | Total energy imported from Mains [kWh]
V41 | MAINS_KWH_YEAR | FLOAT | Energy imported from Mains current year [kWh]
V42 | MAINS_KWH_MONTH | FLOAT | Energy imported from Mains current month [kWh]
V43 | MAINS_KWH_DAY | FLOAT | Energy imported from Mains current day [kWh]
V44 | MAINS_KWH_EXP_TOTAL | FLOAT | Total energy exported to Mains [kWh]
V45 | MAINS_KWH_EXP_YEAR | FLOAT | Energy exported to Mains current year [kWh]
V46 | MAINS_KWH_EXP_MONTH | FLOAT | Energy exported to Mains current month [kWh]
V47 | MAINS_KWH_EXP_DAY | FLOAT | Energy exported to Mains current day [kWh]
V48 | LOAD_KWH_TOTAL | FLOAT | Total energy consumed [kWh]
V49 | LOAD_KWH_YEAR | FLOAT | Energy consumed current year [kWh]
V50 | LOAD_KWH_MONTH | FLOAT | Energy consumed current month [kWh]
V51 | LOAD_KWH_DAY | FLOAT | Energy consumed current day [kWh]
V52 | PV_FUEL_SAVE_TOTAL | FLOAT | Fuel volume saving total [user defined, default: liter]
V53 | PV_FUEL_SAVE_YEAR | FLOAT | Fuel volume saving current year [user defined, default: liter]
V54 | PV_FUEL_SAVE_MONTH | FLOAT | Fuel volume saving current month [user defined, default: liter]
V55 | PV_FUEL_SAVE_DAY | FLOAT | Fuel volume saving current day [user defined, default: liter]
V56 | PV_FUEL_EXPEN_SAVE_TOTAL | FLOAT | Fuel expense savings total [user defined, default: euro]
V57 | PV_FUEL_EXPEN_SAVE_YEAR | FLOAT | Fuel expense savings current year [user defined, default: euro]
V58 | PV_FUEL_EXPEN_SAVE_MONTH | FLOAT | Fuel expense savings current month [user defined, default: euro]
V59 | PV_FUEL_EXPEN_SAVE_DAY | FLOAT | Fuel expense savings current day [user defined, default: euro]
V60 | PV_FUEL_EMISS_SAVE_TOTAL | FLOAT | CO2 emission savings total [user defined, default: kg]
V61 | PV_FUEL_EMISS_SAVE_YEAR | FLOAT | CO2 emission savings current year [user defined, default: kg]
V62 | PV_FUEL_EMISS_SAVE_MONTH | FLOAT | CO2 emission savings current month [user defined, default: kg]
V63 | PV_FUEL_EMISS_SAVE_DAY | FLOAT | CO2 emission savings current day [user defined, default: kg]
V64 | PV_EXP_SAVE_TOTAL | FLOAT | PV export yield total [user defined, default: euro]
V65 | PV_EXP_SAVE_YEAR | FLOAT | PV export yield current year [user defined, default: euro]
V66 | PV_EXP_SAVE_MONTH | FLOAT | PV export yield current month [user defined, default: euro]
V67 | PV_EXP_SAVE_DAY | FLOAT | PV export yield current day [user defined, default: euro]
V68 | MAINS_IMP_SAVE_TOTAL | FLOAT | Mains import expense savings total [user defined, default: euro]
V69 | MAINS_IMP_SAVE_YEAR | FLOAT | Mains import expense savings current year [user defined, default: euro]
V70 | MAINS_IMP_SAVE_MONTH | FLOAT | Mains import expense savings current month [user defined, default: euro]
V71 | MAINS_IMP_SAVE_DAY | FLOAT | Mains import expense savings current day [user defined, default: euro]
V72 | DG_FUEL_CON_TOTAL | FLOAT | Fuel volume consumed total [user defined, default: liter]
V73 | DG_FUEL_CON_YEAR | FLOAT | Fuel volume consumed current year [user defined, default: liter]
V74 | DG_FUEL_CON_MONTH | FLOAT | Fuel volume consumed current month [user defined, default: liter]
V75 | DG_FUEL_CON_DAY | FLOAT | Fuel volume consumed current day [user defined, default: liter]
V76 | DG_FUEL_EXPEN_CON_TOTAL | FLOAT | Fuel expense total [user defined, default: euro]
V77 | DG_FUEL_EXPEN_CON_YEAR | FLOAT | Fuel expense current year [user defined, default: euro]
V78 | DG_FUEL_EXPEN_CON_MONTH | FLOAT | Fuel expense current month [user defined, default: euro]
V79 | DG_FUEL_EXPEN_CON_DAY | FLOAT | Fuel expense current day [user defined, default: euro]
V80 | DG_FUEL_EMISS_CON_TOTAL | FLOAT | CO2 emission total [user defined, default: kg]
V81 | DG_FUEL_EMISS_CON_YEAR | FLOAT | CO2 emission current year [user defined, default: kg]
V82 | DG_FUEL_EMISS_CON_MONTH | FLOAT | CO2 emission current month [user defined, default: kg]
V83 | DG_FUEL_EMISS_CON_DAY | FLOAT | CO2 emission current day [user defined, default: kg]
V84 | MAINS_IMP_CON_TOTAL | FLOAT | Mains import expense total [user defined, default: euro]
V85 | MAINS_IMP_CON_YEAR | FLOAT | Mains import expense current year [user defined, default: euro]
V86 | MAINS_IMP_CON_MONTH | FLOAT | Mains import expense current month [user defined, default: euro]
V87 | MAINS_IMP_CON_DAY | FLOAT | Mains import expense current day [user defined, default: euro]
V88 | MAINS_EXP_SAVE_TOTAL | FLOAT | Mains export yield total [user defined, default: euro]
V89 | MAINS_EXP_SAVE_YEAR | FLOAT | Mains export yield current year [user defined, default: euro]
V90 | MAINS_EXP_SAVE_MONTH | FLOAT | Mains export yield current month [user defined, default: euro]
V91 | MAINS_EXP_SAVE_DAY | FLOAT | Mains export yield current day [user defined, default: euro]
V92 | PV_PENETRATION_TOTAL | FLOAT | PV penetration ratio total [%]
V93 | PV_PENETRATION_YEAR | FLOAT | PV penetration ratio current year [%]
V94 | PV_PENETRATION_MONTH | FLOAT | PV penetration ratio current month [%]
V95 | PV_PENETRATION_DAY | FLOAT | PV penetration ratio current day [%]
V96 | PV_PERFORMANCE_TOTAL | FLOAT | PV performance ratio total [%]
V97 | PV_PERFORMANCE_YEAR | FLOAT | PV performance ratio current year [%]
V98 | PV_PERFORMANCE_MONTH | FLOAT | PV performance ratio current month [%]
V99 | PV_PERFORMANCE_DAY | FLOAT | PV performance ratio current day [%]
V100 | P_PV_LOAD_PCT | FLOAT | PV active power loading [%]
V101 | Q_PV_LOAD_PCT | FLOAT | PV reactive power loading [%]
V102 | Q_DG_LOAD_PCT | FLOAT | Genset reactive power loading [%]
V103 | P_MAINS_LOAD_PCT | FLOAT | Mains active power loading [%]
V104 | Q_MAINS_LOAD_PCT | FLOAT | Mains reactive power loading [%]
V105 | P_PV_LOAD_ERR_PCT | FLOAT | PV active power error in regards to reference [%]
V106 | Q_PV_LOAD_ERR_PCT | FLOAT | PV reactive power error in regards to reference [%]
V107 | P_DG_LOAD_ERR_PCT | FLOAT | Genset active power error in regards to reference [%]
V108 | Q_DG_LOAD_ERR_PCT | FLOAT | Genset reactive power error in regards to reference [%]
V109 | P_MAINS_LOAD_ERR_PCT | FLOAT | Mains active power error in regards to reference [%]
V110 | Q_MAINS_LOAD_ERR_PCT | FLOAT | Mains reactive power error in regards to reference [%]
V111 | SITE | CHAR(80) | Site name typed in on project into page on ECweb
V112 | CUSTOMER | CHAR(80) | Customer name typed in on project into page on ECweb
V113 | INSTALLER | CHAR(80) | Installer name typed in on project into page on ECweb
V114 | INSTALL_DATE | CHAR(80) | Instalation date typed in on project into page on ECweb
V115 | COUNTRY | CHAR(80) | County typed in on project into page on ECweb
V116 | REGION | CHAR(80) | Region typed in on project into page on ECweb
V117 | CITY | CHAR(80) | City typed in on project into page on ECweb
V118 | LATITUDE | FLOAT | Latitude GPS coordinate
V119 | LONGITUDE | FLOAT | Longitude GPS coordinate
V120..V151 | INVERTER_P_POWER | INT | Inverter 1 to 32 active power [W]
V152..V183 | INVERTER_Q_POWER | INT | Inverter 1 to 32 reactive power [VAr]
V184..V215 | INVERTER_SN | CHAR(32) | Inverter 1 to 32 serial number
V216..V247 | INVERTER_MODEL | CHAR(32) | Inverter 1 to 32 model
V248..V279 | INVERTER_WH | INT UNSIGNED | Inverter 1 to 32 energy produced total [kWh]
V280..V311 | INVERTER_L1N | SMALLINT UNSIGNED | Inverter 1 to 32 Line1-neutral voltage [0.1V]
V312..V343 | INVERTER_L1L2 | SMALLINT UNSIGNED | Inverter 1 to 32 Line1-Line2 voltage [0.1V]
V344..V375 | INVERTER_HZ | SMALLINT UNSIGNED | Inverter 1 to 32 Line frequency [0.01Hz]
V376..V407 | INVERTER_STATE | SMALLINT UNSIGNED | Inverter 1 to 32 operation state
V408..V439 | INVERTER_CAB_TEMP | SMALLINT | Inverter 1 to 32 cabinet temperature [0.1C]
V440..V471 | INVERTER_INP_01_DCA | SMALLINT UNSIGNED | Inverter 1 to 32 DC current input1 [0.1A]
V472..V503 | INVERTER_INP_01_DCU | SMALLINT UNSIGNED | Inverter 1 to 32 DC voltage input1 [0.1V]
V504..V535 | INVERTER_INP_02_DCA | SMALLINT UNSIGNED | Inverter 1 to 32 DC current input2 [0.1A]
V536..V567 | INVERTER_INP_02_DCU | SMALLINT UNSIGNED | Inverter 1 to 32 DC voltage input2 [0.1V]
V568..V599 | INVERTER_INP_03_DCA | SMALLINT UNSIGNED | Inverter 1 to 32 DC current input3 [0.1A]
V600..V631 | INVERTER_INP_03_DCU | SMALLINT UNSIGNED | Inverter 1 to 32 DC voltage input3 [0.1V]
V632..V663 | INVERTER_INP_04_DCA | SMALLINT UNSIGNED | Inverter 1 to 32 DC current input4 [0.1A]
V664..V695 | INVERTER_INP_04_DCU | SMALLINT UNSIGNED | Inverter 1 to 32 DC voltage input4 [0.1V]
V696..V711 | DG_METER_P_POWER | INT | DG power meter 1 to 16 active power [W]
V712..V727 | DG_METER_Q_POWER | INT | DG power meter 1 to 16 reactive power [VAr]
V728..V743 | PV_METER_P_POWER | INT | PV power meter 1 to 16 active power [W]
V744..V759 | PV_METER_Q_POWER | INT | PV power meter 1 to 16 reactive power [VAr]
V760..V775 | MAINS_METER_P_POWER | INT | PV power meter 1 to 16 active power [W]
V776..V791 | MAINS_METER_Q_POWER | INT | PV power meter 1 to 16 reactive power [VAr]
V792 | SENSOR_GHI | FLOAT | GHI irradiance [W/m2]
V793 | SENSOR_AMB_TEMP | FLOAT | Ambient temperature [C]
V794 | SENSOR_WND_SPD | FLOAT | Wind speed [m/s]
V795 | SENSOR_RH | FLOAT | Relative humidity [%]
V796 | SENSOR_PRES | FLOAT | Barometrical pressure [HPa]
V797 | SENSOR_WND_DIR | FLOAT | Wind direction [deg]
V798 | SENSOR_RAIN | FLOAT | Rain fall [mm]
V799 | LATITUDELONGITUDE | CHAR(20) | (Latitude, Longitude) GPS coordinates seperated by komma
V800 | CURRENCY | CHAR(10) | Selected currency
V801 | VOLUME | CHAR(10) | Selected measure for volume
V802 | MASS | CHAR(10) | Selected measure for mass
V803 | NBR_INVERTERS | SMALLINT UNSIGNED | Number of inverter
V804 | NBR_DG_METERS | SMALLINT UNSIGNED | Number of dg meters
V805 | NBR_PV_METERS | SMALLINT UNSIGNED | Number of pv meters
V806 | NBR_MAINS_METERS | SMALLINT UNSIGNED | Number of mains meters
V807 | SENSORS_ENABLED | SMALLINT UNSIGNED | Bitwise 0: POA 1: BOM 2: GHI 3: Ambient temp. 4: Wind speed 5: Relative humidity 6: Bar pressure 7: Wind direction 8: Rain
V808 | INSTALLED_P_CAPACITY | FLOAT | installed panel capacity in kW
V809 | INVERTERS_01-16_MISSING | SMALLINT UNSIGNED | Bitwise
V810 | INVERTERS_17-32_MISSING | SMALLINT UNSIGNED | Bitwise
V811 | DG_METER_01-16_MISSING | SMALLINT UNSIGNED | Bitwise
V812 | PV_METER_01-16_MISSING | SMALLINT UNSIGNED | Bitwise
V813 | MAINS_METER_01-16_MISSING | SMALLINT UNSIGNED | Bitwise
V814 | INVERTER_PROTOCOL_SELECTED | SMALLINT UNSIGNED | Inverter protocol selected
V815 | DG_METER_PROTOCOL_SELECTED | SMALLINT UNSIGNED | Genset meter protocol selected
V816 | PV_METER_PROTOCOL_SELECTED | SMALLINT UNSIGNED | PV meter protocol selected
V817 | MAINS_METER_PROTOCOL_SELECTED | SMALLINT UNSIGNED | Mains meter protocol selected