## Input Register 0x04
Mains Power meter
Address | DataLabel | DataType | Description | Not available value
6400..6401 | ACP | 32 signed int (byte order: ABCD) | AC Power total [W] | 0x80000000
6402..6403 | ACQ | 32 signed int (byte order: ABCD) | AC Reactive power total [VAr] | 0x80000000
6404..6405 | ACS | 32 signed int (byte order: ABCD) | AC Apperant power total [VA] | 0x80000000
6406..6407 | PF | 32 signed int (byte order: ABCD) | Power factor total [0.001] | 0x80000000
6408..6409 | ACP1 | 32 signed int (byte order: ABCD) | AC Power line1 [W] | 0x80000000
6410..6411 | ACP2 | 32 signed int (byte order: ABCD) | AC Power line2 [W] | 0x80000000
6412..6413 | ACP3 | 32 signed int (byte order: ABCD) | AC Power line3 [W] | 0x80000000
6414..6415 | ACQ1 | 32 signed int (byte order: ABCD) | AC Reactive power line1 [VAr] | 0x80000000
6416..6417 | ACQ2 | 32 signed int (byte order: ABCD) | AC Reactive power line2 [VAr] | 0x80000000
6418..6419 | ACQ3 | 32 signed int (byte order: ABCD) | AC Reactive power line3 [VAr] | 0x80000000
6420..6421 | ACS1 | 32 signed int (byte order: ABCD) | AC Apperant power line1 [VA] | 0x80000000
6422..6423 | ACS2 | 32 signed int (byte order: ABCD) | AC Apperant power line2 [VA] | 0x80000000
6424..6425 | ACS3 | 32 signed int (byte order: ABCD) | AC Apperant power line3 [VA] | 0x80000000
6426..6427 | PF1 | 32 signed int (byte order: ABCD) | Power factor line1 [0.001] | 0x80000000
6428..6429 | PF2 | 32 signed int (byte order: ABCD) | Power factor line2 [0.001] | 0x80000000
6430..6431 | PF3 | 32 signed int (byte order: ABCD) | Power factor line3 [0.001] | 0x80000000
6432..6433 | L1L2 | 32 unsigned int (byte order: ABCD) | Line1-line2 voltage [0.1V] | 0xFFFFFFFF
6434..6435 | L2L3 | 32 unsigned int (byte order: ABCD) | Line2-line3 voltage [0.1V] | 0xFFFFFFFF
6436..6437 | L3L1 | 32 unsigned int (byte order: ABCD) | Line3-line1 voltage [0.1V] | 0xFFFFFFFF
6438..6439 | L1N | 32 unsigned int (byte order: ABCD) | Line1-neutral voltage [0.1V] | 0xFFFFFFFF
6440..6441 | L2N | 32 unsigned int (byte order: ABCD) | Line2-neutral voltage [0.1V] | 0xFFFFFFFF
6442..6443 | L3N | 32 unsigned int (byte order: ABCD) | Line3-neutral voltage [0.1V] | 0xFFFFFFFF
6444..6445 | L1A | 32 unsigned int (byte order: ABCD) | line1 current [mA] | 0xFFFFFFFF
6446..6447 | L2A | 32 unsigned int (byte order: ABCD) | line2 current [mA] | 0xFFFFFFFF
6448..6449 | L3A | 32 unsigned int (byte order: ABCD) | line3 current [mA] | 0xFFFFFFFF
6450..6451 | LNA | 32 unsigned int (byte order: ABCD) | Neutral current [mA] | 0xFFFFFFFF
6452..6453 | L1HZ | 32 unsigned int (byte order: ABCD) | Line1 frequency [0.01Hz] | 0xFFFFFFFF
6454..6455 | L2HZ | 32 unsigned int (byte order: ABCD) | Line2 frequency [0.01Hz] | 0xFFFFFFFF
6456..6457 | L3HZ | 32 unsigned int (byte order: ABCD) | Line1 frequency [0.01Hz] | 0xFFFFFFFF
6458..6459 | KWH_TOT | 32 unsigned int (byte order: ABCD) | Total energy [kWh] | 0xFFFFFFFF
6460..6461 | KWH_IMP | 32 unsigned int (byte order: ABCD) | Toatl energy imported [kWh] | 0xFFFFFFFF
6462..6463 | KWH_EXP | 32 unsigned int (byte order: ABCD) | Toatl energy exported [kWh] | 0xFFFFFFFF
6464..6465 | KVARH_TOT | 32 unsigned int (byte order: ABCD) | Total reactive energy [kVArh] | 0xFFFFFFFF
6466..6467 | KVARH_IND | 32 unsigned int (byte order: ABCD) | Total reactive inductive energy [kVArh] | 0xFFFFFFFF
6468..6469 | KVARH_CAP | 32 unsigned int (byte order: ABCD) | Total reactive capacitive energy [kVArh] | 0xFFFFFFFF
6470..6596 | RESERVED | Not defined | Reserved for later use | Not defined
6597 | DIG_STATUS | 16 unsigned int | Bitwise | Not defined
6598 | MB_POSITION | 16 unsigned int | 0: MB Off 1: MB On | Not defined
6599 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
IO module number 1 to 4 The addressses of module number x is found by: AddressModule_x = (x-1) * 50 + Address
Address | DataLabel | DataType | Description | Not available value
20500 | INPUT_1_16 | 16 unsigned int | bitwise | Not defined
20501 | OUTPUT_1_16 | 16 unsigned int | bitwise | Not defined
20502..20503 | AIO_INPUT_01 | FLOAT (byte order: ABCD) | Analogue input 01 | Not defined
20504..20505 | AIO_INPUT_02 | FLOAT (byte order: ABCD) | Analogue input 02 | Not defined
20506..20507 | AIO_INPUT_03 | FLOAT (byte order: ABCD) | Analogue input 03 | Not defined
20508-20509 | AIO_INPUT_04 | FLOAT (byte order: ABCD) | Analogue input 04 | Not defined
20510..20511 | AIO_INPUT_05 | FLOAT (byte order: ABCD) | Analogue input 05 | Not defined
20512..20513 | AIO_INPUT_06 | FLOAT (byte order: ABCD) | Analogue input 06 | Not defined
20514..20515 | AIO_INPUT_07 | FLOAT (byte order: ABCD) | Analogue input 07 | Not defined
20516..20517 | AIO_INPUT_08 | FLOAT (byte order: ABCD) | Analogue input 08 | Not defined
20518..20519 | AIO_OUTPUT_01 | FLOAT (byte order: ABCD) | Analogue output 01 | Not defined
20520..20521 | AIO_OUTPUT_02 | FLOAT (byte order: ABCD) | Analogue output 02 | Not defined
20522..20523 | AIO_OUTPUT_03 | FLOAT (byte order: ABCD) | Analogue output 03 | Not defined
20524..20525 | AIO_OUTPUT_04 | FLOAT (byte order: ABCD) | Analogue output 04 | Not defined
20526..20527 | AIO_OUTPUT_05 | FLOAT (byte order: ABCD) | Analogue output 05 | Not defined
20528..20529 | AIO_OUTPUT_06 | FLOAT (byte order: ABCD) | Analogue output 06 | Not defined
20530..20531 | AIO_OUTPUT_07 | FLOAT (byte order: ABCD) | Analogue output 07 | Not defined
20532..20533 | AIO_OUTPUT_08 | FLOAT (byte order: ABCD) | Analogue output 08 | Not defined
20534 | CH_CONF_01 | 16 unsigned int | Channel confirguration 01 | Not defined
20535 | CH_CONF_02 | 16 unsigned int | Channel confirguration 02 | Not defined
20536 | CH_CONF_03 | 16 unsigned int | Channel confirguration 03 | Not defined
20537 | CH_CONF_04 | 16 unsigned int | Channel confirguration 04 | Not defined
20538 | CH_CONF_05 | 16 unsigned int | Channel confirguration 05 | Not defined
20539 | CH_CONF_06 | 16 unsigned int | Channel confirguration 06 | Not defined
20540 | CH_CONF_07 | 16 unsigned int | Channel confirguration 07 | Not defined
20541 | CH_CONF_08 | 16 unsigned int | Channel confirguration 08 | Not defined
20542 | CH_STATUS | 16 unsigned int | Channel status | Not defined
20543 | MOD_TEMP | 16 unsigned int | Module temperature [0.1C] | Not defined
20544..20548 | RESERVED | Not defined | Reserved for later use | Not defined
20549 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
Grid support - frequency
22200..22201 | FREQ | FLOAT (byte order: ABCD) | Grid frequency [Hz] | Not defined
22202..22203 | P_BAT | FLOAT (byte order: ABCD) | Battery power [kW] | Not defined
22204..22205 | P_BAT_PCT | FLOAT (byte order: ABCD) | Battery power percentage of the total service capacity [%] | Not defined
22206..22207 | FCR_TOT_P_COMP | FLOAT (byte order: ABCD) | FCR total compensation [kW] | Not defined
22208..22209 | FCR_N_CAP | FLOAT (byte order: ABCD) | FCR-N capacity [kW] | Not defined
22210..22211 | FCR_N_F_COMP | FLOAT (byte order: ABCD) | Frequency compensation from FCR-N [Hz] | Not defined
22212..22213 | FCR_N_P_COMP | FLOAT (byte order: ABCD) | Power compensation from FCR-N [kW] | Not defined
22214..22215 | FCR_D_CAP_DO | FLOAT (byte order: ABCD) | FCR-D Down capacity [kW] | Not defined
22216..22217 | FCR_D_CAP_UP | FLOAT (byte order: ABCD) | FCR-D Up capacity [kW] | Not defined
22218..22219 | FCR_D_F_COMP | FLOAT (byte order: ABCD) | Frequency compensation from FCR-D [Hz] | Not defined
22220..22221 | FCR_D_P_COMP | FLOAT (byte order: ABCD) | Power compensation power FCR-D [kW] | Not defined
22222 | NEM_CURRENT_FCR_N_UP_ALLOWED | 16 unsigned int | NEM Current for FCR-N Upper allowed 0: Not allowed 1: Allowed | Not defined
22223 | NEM_CURRENT_FCR_N_LO_ALLOWED | 16 unsigned int | NEM Current for FCR-N Lower allowed 0: Not allowed 1: Allowed | Not defined
22224..22225 | NEM_CURRENT_FCR_N | FLOAT (byte order: ABCD) | NEM FCR-N current value in [0;1] range | Not defined
22226..22227 | NEM_FCR_N_P_COMP | FLOAT (byte order: ABCD) | NEM FCR-N Power compensation [kW] | Not defined
22228 | NEM_CURRENT_FCR_D_UP_ALLOWED | 16 unsigned int | NEM Current for FCR-D Upper allowed 0: Not allowed 1: Allowed | Not defined
22229 | NEM_CURRENT_FCR_D_LO_ALLOWED | 16 unsigned int | NEM Current for FCR-D Lower allowed 0: Not allowed 1: Allowed | Not defined
22230..22231 | NEM_CURRENT_FCR_D | FLOAT (byte order: ABCD) | NEM FCR-D current value in [0;1] range | Not defined
22232..22233 | NEM_FCR_D_P_COMP | FLOAT (byte order: ABCD) | NEM FCR-D Power compensation [kW] | Not defined
22234..22235 | NEM_FCR_COMP_P_TOT | FLOAT (byte order: ABCD) | NEM FCR Total power compensation [kW] | Not defined
22236 | AEM_UPPER_ALLOWED | 16 unsigned int | AEM Upper allowed 0: Not allowed 1: Allowed | Not defined
22237 | AEM_LOWER_ALLOWED | 16 unsigned int | AEM Lower allowed 0: Not allowed 1: Allowed | Not defined
22238..22239 | AEM_FREF | FLOAT (byte order: ABCD) | Frequency reference for the FCR generated by AEM [Hz] | Not defined
22240..22241 | AEM_COMP | FLOAT (byte order: ABCD) | Frequency compensation for the FCR generated by AEM [Hz] | Not defined
22242..22243 | FCR_NEMAEM_TOT_COMP_HI | FLOAT (byte order: ABCD) | Battery total FCR compensation inclusive NEM and AEM [kW] | Not defined
22244..22245 | SOC | FLOAT (byte order: ABCD) | Battery SOC [%} | Not defined
22246..22247 | MIN_LEFT | FLOAT (byte order: ABCD) | Time left in battery with full dicsharge [minutes] | Not defined
22248..22249 | FFR_CAP | FLOAT (byte order: ABCD) | FFR capacity [kW] | Not defined
22250..22251 | FFR_P_COMP | FLOAT (byte order: ABCD) | Power compensation from FFR [kW] | Not defined
22252..22253 | BAT_RATED_H | FLOAT (byte order: ABCD) | Battery rated hours [h] | Not defined
22254..22255 | AFRR_CAP_UP | FLOAT (byte order: ABCD) | AFFR Up capacity [kW] | Not defined
22256..22257 | AFRR_CAP_DOWN | FLOAT (byte order: ABCD) | AFFR Down capacity [kW] | Not defined
22258..22259 | AFRR_P_COMP | FLOAT (byte order: ABCD) | Power compensation from aFFR [kW] | Not defined
22260..22261 | MFRR_CAP | FLOAT (byte order: ABCD) | mFFR capacity [kW] | Not defined
22262..22263 | mFRR_P_COMP | FLOAT (byte order: ABCD) | Power compensation from mFFR [kW] | Not defined
22264..22299 | Reserved | Not defined | Reserved for later use | Not defined
COMMAND PANEL TEXTS
27000..27079 | TEXT_CMD_PANEL_BUTTON 01..04 | string | User configurable texts for command panel button 01..04 | Not defined
27080..27159 | TEXT_CMD_PANEL_BUTTON 05..08 | string | User configurable texts for command panel button 05..08 | Not defined
27160..27239 | TEXT_CMD_PANEL_BUTTON 09..12 | string | User configurable texts for command panel button 09..12 | Not defined
27240..27319 | TEXT_CMD_PANEL_BUTTON 13..16 | string | User configurable texts for command panel button 13..16 | Not defined
27320..27399 | TEXT_CMD_PANEL_LED 01..04 | string | User configurable texts for command panel led 01..04 | Not defined
27400..27479 | TEXT_CMD_PANEL_LED 05..08 | string | User configurable texts for command panel led 05..08 | Not defined
27480..27559 | TEXT_CMD_PANEL_LED 09..12 | string | User configurable texts for command panel led 09..12 | Not defined
27560..27639 | TEXT_CMD_PANEL_LED 13..16 | string | User configurable texts for command panel led 13..16 | Not defined
27640..27999 | RESERVED | Not defined | Reserved for later use | Not defined
ECLOGIC BUILDER AREA 1
28000 | Q1 gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28001 | Q2 gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28002 | Q3 gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28003 | Q-out gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28004 | Inverted Q-out gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28005..28099 | RESERVED | Not defined | Reserved for later use | Not defined
Frequency Service Schedules Area
28100 | FREQMARKET_BIT_STATUS | 16 unsigned int | BIT0: Frequency Service Schedule Valid BIT1: Frequency Service 60min resolution BIT2: Frequency Service 15min resolution | Not defined
28101..28148 | FREQMARKET_FCR_MWH | FLOAT (byte order: ABCD) | FCR capacity schedule (24h or 6h period depending on resolution) [MW] | Not defined
28149..28196 | FREQMARKET_FCR_N_MWH | FLOAT (byte order: ABCD) | FCR-N capacity schedule (24h or 6h period depending on resolution) [MW] | Not defined
28197..28244 | FREQMARKET_FCR_D_UP_MWH | FLOAT (byte order: ABCD) | FCR-D Upwards capacity schedule (24h or 6h period depending on resolution) [MW] | Not defined
28245..28292 | FREQMARKET_FCR_D_DOWN_MWH | FLOAT (byte order: ABCD) | FCR-D Downwards capacity schedule (24h or 6h period depending on resolution) [MW] | Not defined
28293..28340 | FREQMARKET_FFR_MWH | FLOAT (byte order: ABCD) | FFR capacity schedule (24h or 6h period depending on resolution) [MW] | Not defined
28341..28388 | FREQMARKET_AFRR_UP_MWH | FLOAT (byte order: ABCD) | aFFR Upwards capacity schedule (24h or 6h period depending on resolution) [MW] | Not defined
28389..28436 | FREQMARKET_AFRR_DOWN_MWH | FLOAT (byte order: ABCD) | aFFR Downwards capacity schedule (24h or 6h period depending on resolution) [MW] | Not defined
28437..28484 | FREQMARKET_MFRR_MWH | FLOAT (byte order: ABCD) | mFFR Upwards capacity schedule (24h or 6h period depending on resolution) [MW] | Not defined
ECLOGIC LINKER COMMAND AREA 1
29000 | MB ON 1-16 | 16 unsigned int | bitwise | Not defined
29001 | Relay 1-16 on all Mains meters | 16 unsigned int | bitwise | Not defined
29002 | Relay 1-16 on Mains meter 1 | 16 unsigned int | bitwise | Not defined
29003 | Relay 1-16 on all IO modules | 16 unsigned int | bitwise | Not defined
29004 | Relay 1-16 on IO module 1 | 16 unsigned int | bitwise | Not defined
29005 | Relay 1-16 on IO module 2 | 16 unsigned int | bitwise | Not defined
29006 | Relay 1-16 on IO module 3 | 16 unsigned int | bitwise | Not defined
29007 | Relay 1-16 on IO module 4 | 16 unsigned int | bitwise | Not defined
29009 | SOC Set flip flop 1-8 | 16 unsigned int | bitwise | Not defined
29010 | SOC Reset flip flop 1-8 | 16 unsigned int | bitwise | Not defined
29011 | Cmd panel LED 01..16: Green | 16 unsigned int | bitwise | Not defined
29012 | Cmd panel LED 01..16: Red | 16 unsigned int | bitwise | Not defined
29013 | EClogic Alarms 01..08 | 16 unsigned int | bitwise | Not defined
29014 | EClogic Timers 01..08 | 16 unsigned int | bitwise | Not defined
29015..29799 | RESERVED | Not defined | Reserved for later use | Not defined
MISC AREA 1
Address | DataLabel | DataType | Description | Not available value
30000..30001 | POWER_P_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total Mains active power [kW] | Not defined
30002..30003 | POWER_Q_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total Mains reactive power [kVAr] | Not defined
30004..30005 | POWER_S_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total Mains apperant power [kVAr] | Not defined
30006..30007 | POWER_COSPHI_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total Mains cosphi | Not defined
30008 | IND_CAP_MAINS | 16 unsigned int | 0: Capacitive 1: Inductive | Not defined
30009..30010 | POWER_P_BAT_TOTAL | FLOAT (byte order: ABCD) | Total battery active power [kW] | Not defined
30999 | ECPV_SW_VERSION | 16 unsigned int | SW version opf the Ecpv application SW
BITFIELD AREA 1
31000 | BITFIELD_1 | 16 unsigned int | BIT0: Any MB ON | Not defined
31001 | BITFIELD_ 2 | 16 unsigned int | BIT0: Any Mains meter missing BIT1: Mains meter socket connection alarm BIT2: EMS missing BIT3: EMS socket connection alarm BIT4: IO1 missing BIT5: IO2 missing BIT6: IO3 missing BIT7: IO4 missing BIT15: Common comm. alarm | Not defined
31002 | BITFIELD_3 | 16 unsigned int | EClogic Threshold output 01..16 | Not defined
31003 | BITFIELD_4 | 16 unsigned int | BIT0: Command timer 01 active BIT1: Command timer 02 active BIT2: Command timer 03 active BIT3: Command timer 04 active | Not defined
31004 | BITFIELD_5 | 16 unsigned int | Command Panel buttons 01..16 | Not defined
31005 | BITFIELD_6 | 16 unsigned int | EClogic Timers elapsed 01..16 | Not defined
31006 | BITFIELD_7 | 16 unsigned int | EClogic Modbus Event 01..16 | Not defined
31007 | BITFIELD_8 | 16 unsigned int | EClogic Modbus Event 17..32 | Not defined
31008 | BITFIELD_9 | 16 unsigned int | BIT0: EClogic alarm 01 active BIT1:EClogic alarm 02 active BIT2: EClogic alarm 03 active BIT3: EClogic alarm 04 active BIT4: EClogic alarm 05 active BIT5:EClogic alarm 06 active BIT6: EClogic alarm 07 active BIT7: EClogic alarm 08 active | Not defined
31008 | BITFIELD_9 | 16 unsigned int | ECapi EClogic event 01 | Not defined
31009 | BITFIELD_10 | 16 unsigned int | ECapi EClogic event 02 | Not defined
SETTINGS AREA
31700 | NBR_MAINS_METERS | 16 unsigned int | Number of mains meters | Not defined
31701 | MAINS_METER_PROTOCOL_SELECTED | 16 unsigned int | Mains meter protocol selected | Not defined
31702 | IOS_ENABLED | 16 unsigned int | Bitwise 0: IO module 1 1: IO module 2 2: IO module 3 3: IO module 4 | Not defined
31703 | EMS_PROTOCOL_SELECTED | 16 unsigned int | EMS protocol selected | Not defined
31704 | FREQ_SERV_SYNC_AREA | 16 unsigned int | 0: Nordic sync. Area 1: Central europe sync. Area | Not defined
RTC CLOCK
32000 | Year | 16 unsigned int | ECpv RTC year | Not defined
32001 | Month | 16 unsigned int | ECpv RTC month | Not defined
32002 | Date | 16 unsigned int | ECpv RTC date | Not defined
32003 | Hour | 16 unsigned int | ECpv RTC hour | Not defined
32004 | Minute | 16 unsigned int | ECpv RTC minute | Not defined
32005 | Second | 16 unsigned int | ECpv RTC second | Not defined
32006 | Millisecond | 16 unsigned int | ECpv RTC millisecond | Not defined
IO MODULE INFO
32010 | IO_TYPE_01 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32011 | IO_TYPE_02 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32012 | IO_TYPE_03 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32013 | IO_TYPE_04 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32014 | IO_ANALOGUE_TYPE_SELECTED | 16 unsigned int | BIT0: Module 1 is analogue type BIT1: Module 2 is analogue type BIT2: Module 3 is analogue type BIT3: Module 4 is analogue type
32020..32039 | INFOTEXT_MODULE_01 | string | Info text for Module 1 type | Not defined
32040..32059 | INFOTEXT_MODULE_02 | string | Info text for Module 2 type | Not defined
32060..32079 | INFOTEXT_MODULE_03 | string | Info text for Module 3 type | Not defined
32080..32099 | INFOTEXT_MODULE_04 | string | Info text for Module 4 type | Not defined
STAUS TEXTS
32400..32479 | STATUS_TEXT_01 | string | Status text in line 1 | Not defined
32480..32559 | STATUS_TEXT_02 | string | Status text in line 2 | Not defined
32560..32639 | STATUS_TEXT_03 | string | Status text in line 3 | Not defined
32640 | STATUS_TEXT_01_ACK_POSSIBLE | enum16 | 0: NOT POSSIBLE 1: POSSIBLE | Not defined
32641 | STATUS_TEXT_02_ACK_POSSIBLE | enum16 | 0: NOT POSSIBLE 1: POSSIBLE | Not defined
32642 | STATUS_TEXT_03_ACK_POSSIBLE | enum16 | 0: NOT POSSIBLE 1: POSSIBLE | Not defined
32643 | NBR_OF_STATUS_TEXTS | 16 unsigned int | Number of status texts displayed | Not defined
32644 | MIN_SLIDER | 16 signed int | Minimum possible status text slider value | Not defined

## Holding Register 0x03
Proprietary profile
Address | DataLabel | DataType | Description | Note
Commands
1000 | FreqServiceTimeOffsetDisplay | 16 unsigned int | Time interval to be displayed in webserver and HMI as well as copied to modbus area when the Frequency Service Schedules are of 15min resolution. 0: 00:00h-05:59h 1: 06:00h-11:59h 2: 12:00h-17:59h 3: 18:00h-23:59h
Relay control
3000 | Relay 1-16 on all Mains meters | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3001 | Relay 1-16 on Mains meter 1 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3002 | EClogic Modbus Event 01-16 | 16 unsigned int | bitwise | Maps to input register page for use in Eclogic
3003 | EClogic Modbus Event 17-32 | 16 unsigned int | bitwise | Maps to input register page for use in Eclogic
3004..3999 | Reserved
aFRR/mFRR control
4000..4001 | aFRR Down capacity | FLOAT (byte order: ABCD) | aFRR Downwards capacity [kW] | aFRR functionality must be enabled
4002..4003 | aFRR Up capacity | FLOAT (byte order: ABCD) | aFRR Upwards capacity [kW] | aFRR functionality must be enabled
4004..4005 | aFRR Power cmd | FLOAT (byte order: ABCD) | aFRR Power command [kW] | aFRR functionality must be enabled
4006 | aFRR Power Cmd active | 16 unsigned int | BIT0: aFRR command active | aFRR functionality must be enabled
4007..4008 | mFRR capacity | FLOAT (byte order: ABCD) | mFRR capacity [kW] | aFRR functionality must be enabled
4009..4010 | mFRR Power cmd | FLOAT (byte order: ABCD) | mFRR Power command [kW] | aFRR functionality must be enabled
4011 | mFRR Power Cmd active | 16 unsigned int | BIT0: mFRR command active | aFRR functionality must be enabled
4012..4999 | Reserved