## Input Register 0x04
Genset Power meter number 1 to 16 The addressses of genset meter number x is found by: AddressMeter_x = (x-1) * 200 + Address
Address | DataLabel | DataType | Description | Not available value
0..1 | ACP | 32 signed int (byte order: ABCD) | AC Power total [W] | 0x80000000
2..3 | ACQ | 32 signed int (byte order: ABCD) | AC Reactive power total [VAr] | 0x80000000
4..5 | ACS | 32 signed int (byte order: ABCD) | AC Apperant power total [VA] | 0x80000000
6..7 | PF | 32 signed int (byte order: ABCD) | Power factor total [0.001] | 0x80000000
8..9 | ACP1 | 32 signed int (byte order: ABCD) | AC Power line1 [W] | 0x80000000
10..11 | ACP2 | 32 signed int (byte order: ABCD) | AC Power line2 [W] | 0x80000000
12..13 | ACP3 | 32 signed int (byte order: ABCD) | AC Power line3 [W] | 0x80000000
14..15 | ACQ1 | 32 signed int (byte order: ABCD) | AC Reactive power line1 [VAr] | 0x80000000
16..17 | ACQ2 | 32 signed int (byte order: ABCD) | AC Reactive power line2 [VAr] | 0x80000000
18..19 | ACQ3 | 32 signed int (byte order: ABCD) | AC Reactive power line3 [VAr] | 0x80000000
20..21 | ACS1 | 32 signed int (byte order: ABCD) | AC Apperant power line1 [VA] | 0x80000000
22..23 | ACS2 | 32 signed int (byte order: ABCD) | AC Apperant power line2 [VA] | 0x80000000
24..25 | ACS3 | 32 signed int (byte order: ABCD) | AC Apperant power line3 [VA] | 0x80000000
26..27 | PF1 | 32 signed int (byte order: ABCD) | Power factor line1 [0.001] | 0x80000000
28..29 | PF2 | 32 signed int (byte order: ABCD) | Power factor line2 [0.001] | 0x80000000
30..31 | PF3 | 32 signed int (byte order: ABCD) | Power factor line3 [0.001] | 0x80000000
32..33 | L1L2 | 32 unsigned int (byte order: ABCD) | Line1-line2 voltage [0.1V] | 0xFFFFFFFF
34..35 | L2L3 | 32 unsigned int (byte order: ABCD) | Line2-line3 voltage [0.1V] | 0xFFFFFFFF
36..37 | L3L1 | 32 unsigned int (byte order: ABCD) | Line3-line1 voltage [0.1V] | 0xFFFFFFFF
38..39 | L1N | 32 unsigned int (byte order: ABCD) | Line1-neutral voltage [0.1V] | 0xFFFFFFFF
40..41 | L2N | 32 unsigned int (byte order: ABCD) | Line2-neutral voltage [0.1V] | 0xFFFFFFFF
42..43 | L3N | 32 unsigned int (byte order: ABCD) | Line3-neutral voltage [0.1V] | 0xFFFFFFFF
44..45 | L1A | 32 unsigned int (byte order: ABCD) | line1 current [mA] | 0xFFFFFFFF
46..47 | L2A | 32 unsigned int (byte order: ABCD) | line2 current [mA] | 0xFFFFFFFF
48..49 | L3A | 32 unsigned int (byte order: ABCD) | line3 current [mA] | 0xFFFFFFFF
50..51 | LNA | 32 unsigned int (byte order: ABCD) | Neutral current [mA] | 0xFFFFFFFF
52..53 | L1HZ | 32 unsigned int (byte order: ABCD) | Line1 frequency [0.01Hz] | 0xFFFFFFFF
54..55 | L2HZ | 32 unsigned int (byte order: ABCD) | Line2 frequency [0.01Hz] | 0xFFFFFFFF
56..57 | L3HZ | 32 unsigned int (byte order: ABCD) | Line1 frequency [0.01Hz] | 0xFFFFFFFF
58..59 | KWH_TOT | 32 unsigned int (byte order: ABCD) | Total energy [kWh] | 0xFFFFFFFF
60..61 | KWH_IMP | 32 unsigned int (byte order: ABCD) | Toatl energy imported [kWh] | 0xFFFFFFFF
62..63 | KWH_EXP | 32 unsigned int (byte order: ABCD) | Toatl energy exported [kWh] | 0xFFFFFFFF
64..65 | KVARH_TOT | 32 unsigned int (byte order: ABCD) | Total reactive energy [kVArh] | 0xFFFFFFFF
66..67 | KVARH_IND | 32 unsigned int (byte order: ABCD) | Total reactive inductive energy [kVArh] | 0xFFFFFFFF
68..69 | KVARH_CAP | 32 unsigned int (byte order: ABCD) | Total reactive capacitive energy [kVArh] | 0xFFFFFFFF
70..196 | RESERVED | Not defined | Reserved for later use | Not defined
197 | DIG_STATUS | 16 unsigned int | Bitwise | Not defined
198 | GB_POSITION | 16 unsigned int | 0: GB Off 1: GB On | Not defined
199 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
PV Power meter number 1 to 16 The addressses of PV meter number x is found by: AddressMeter_x = (x-1) * 200 + Address
Address | DataLabel | DataType | Description | Not available value
3200..3201 | ACP | 32 signed int (byte order: ABCD) | AC Power total [W] | 0x80000000
3202..3203 | ACQ | 32 signed int (byte order: ABCD) | AC Reactive power total [VAr] | 0x80000000
3204..3205 | ACS | 32 signed int (byte order: ABCD) | AC Apperant power total [VA] | 0x80000000
3206..3207 | PF | 32 signed int (byte order: ABCD) | Power factor total [0.001] | 0x80000000
3208..3209 | ACP1 | 32 signed int (byte order: ABCD) | AC Power line1 [W] | 0x80000000
3210..3211 | ACP2 | 32 signed int (byte order: ABCD) | AC Power line2 [W] | 0x80000000
3212..3213 | ACP3 | 32 signed int (byte order: ABCD) | AC Power line3 [W] | 0x80000000
3214..3215 | ACQ1 | 32 signed int (byte order: ABCD) | AC Reactive power line1 [VAr] | 0x80000000
3216..3217 | ACQ2 | 32 signed int (byte order: ABCD) | AC Reactive power line2 [VAr] | 0x80000000
3218..3219 | ACQ3 | 32 signed int (byte order: ABCD) | AC Reactive power line3 [VAr] | 0x80000000
3220..3221 | ACS1 | 32 signed int (byte order: ABCD) | AC Apperant power line1 [VA] | 0x80000000
3222..3223 | ACS2 | 32 signed int (byte order: ABCD) | AC Apperant power line2 [VA] | 0x80000000
3224..3225 | ACS3 | 32 signed int (byte order: ABCD) | AC Apperant power line3 [VA] | 0x80000000
3226..3227 | PF1 | 32 signed int (byte order: ABCD) | Power factor line1 [0.001] | 0x80000000
3228..3229 | PF2 | 32 signed int (byte order: ABCD) | Power factor line2 [0.001] | 0x80000000
3230..3231 | PF3 | 32 signed int (byte order: ABCD) | Power factor line3 [0.001] | 0x80000000
3232..3233 | L1L2 | 32 unsigned int (byte order: ABCD) | Line1-line2 voltage [0.1V] | 0xFFFFFFFF
3234..3235 | L2L3 | 32 unsigned int (byte order: ABCD) | Line2-line3 voltage [0.1V] | 0xFFFFFFFF
3236..3237 | L3L1 | 32 unsigned int (byte order: ABCD) | Line3-line1 voltage [0.1V] | 0xFFFFFFFF
3238..3239 | L1N | 32 unsigned int (byte order: ABCD) | Line1-neutral voltage [0.1V] | 0xFFFFFFFF
3240..3241 | L2N | 32 unsigned int (byte order: ABCD) | Line2-neutral voltage [0.1V] | 0xFFFFFFFF
3242..3243 | L3N | 32 unsigned int (byte order: ABCD) | Line3-neutral voltage [0.1V] | 0xFFFFFFFF
3244..3245 | L1A | 32 unsigned int (byte order: ABCD) | line1 current [mA] | 0xFFFFFFFF
3246..3247 | L2A | 32 unsigned int (byte order: ABCD) | line2 current [mA] | 0xFFFFFFFF
3248..3249 | L3A | 32 unsigned int (byte order: ABCD) | line3 current [mA] | 0xFFFFFFFF
3250..3251 | LNA | 32 unsigned int (byte order: ABCD) | Neutral current [mA] | 0xFFFFFFFF
3252..3253 | L1HZ | 32 unsigned int (byte order: ABCD) | Line1 frequency [0.01Hz] | 0xFFFFFFFF
3254..3255 | L2HZ | 32 unsigned int (byte order: ABCD) | Line2 frequency [0.01Hz] | 0xFFFFFFFF
3256..3257 | L3HZ | 32 unsigned int (byte order: ABCD) | Line1 frequency [0.01Hz] | 0xFFFFFFFF
3258..3259 | KWH_TOT | 32 unsigned int (byte order: ABCD) | Total energy [kWh] | 0xFFFFFFFF
3260..3261 | KWH_IMP | 32 unsigned int (byte order: ABCD) | Toatl energy imported [kWh] | 0xFFFFFFFF
3262..3263 | KWH_EXP | 32 unsigned int (byte order: ABCD) | Toatl energy exported [kWh] | 0xFFFFFFFF
3264..3265 | KVARH_TOT | 32 unsigned int (byte order: ABCD) | Total reactive energy [kVArh] | 0xFFFFFFFF
3266..3267 | KVARH_IND | 32 unsigned int (byte order: ABCD) | Total reactive inductive energy [kVArh] | 0xFFFFFFFF
3268..3269 | KVARH_CAP | 32 unsigned int (byte order: ABCD) | Total reactive capacitive energy [kVArh] | 0xFFFFFFFF
3270..3396 | RESERVED | Not defined | Reserved for later use | Not defined
3397 | DIG_STATUS | 16 unsigned int | Bitwise | Not defined
3398 | RESERVED | Not defined | Reserved for later use | Not defined
3399 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
Mains Power meter number 1 to 16 The addressses of Mains meter number x is found by: AddressMeter_x = (x-1) * 200 + Address
Address | DataLabel | DataType | Description | Not available value
6400..6401 | ACP | 32 signed int (byte order: ABCD) | AC Power total [W] | 0x80000000
6402..6403 | ACQ | 32 signed int (byte order: ABCD) | AC Reactive power total [VAr] | 0x80000000
6404..6405 | ACS | 32 signed int (byte order: ABCD) | AC Apperant power total [VA] | 0x80000000
6406..6407 | PF | 32 signed int (byte order: ABCD) | Power factor total [0.001] | 0x80000000
6408..6409 | ACP1 | 32 signed int (byte order: ABCD) | AC Power line1 [W] | 0x80000000
6410..6411 | ACP2 | 32 signed int (byte order: ABCD) | AC Power line2 [W] | 0x80000000
6412..6413 | ACP3 | 32 signed int (byte order: ABCD) | AC Power line3 [W] | 0x80000000
6414..6415 | ACQ1 | 32 signed int (byte order: ABCD) | AC Reactive power line1 [VAr] | 0x80000000
6416..6417 | ACQ2 | 32 signed int (byte order: ABCD) | AC Reactive power line2 [VAr] | 0x80000000
6418..6419 | ACQ3 | 32 signed int (byte order: ABCD) | AC Reactive power line3 [VAr] | 0x80000000
6420..6421 | ACS1 | 32 signed int (byte order: ABCD) | AC Apperant power line1 [VA] | 0x80000000
6422..6423 | ACS2 | 32 signed int (byte order: ABCD) | AC Apperant power line2 [VA] | 0x80000000
6424..6425 | ACS3 | 32 signed int (byte order: ABCD) | AC Apperant power line3 [VA] | 0x80000000
6426..6427 | PF1 | 32 signed int (byte order: ABCD) | Power factor line1 [0.001] | 0x80000000
6428..6429 | PF2 | 32 signed int (byte order: ABCD) | Power factor line2 [0.001] | 0x80000000
6430..6431 | PF3 | 32 signed int (byte order: ABCD) | Power factor line3 [0.001] | 0x80000000
6432..6433 | L1L2 | 32 unsigned int (byte order: ABCD) | Line1-line2 voltage [0.1V] | 0xFFFFFFFF
6434..6435 | L2L3 | 32 unsigned int (byte order: ABCD) | Line2-line3 voltage [0.1V] | 0xFFFFFFFF
6436..6437 | L3L1 | 32 unsigned int (byte order: ABCD) | Line3-line1 voltage [0.1V] | 0xFFFFFFFF
6438..6439 | L1N | 32 unsigned int (byte order: ABCD) | Line1-neutral voltage [0.1V] | 0xFFFFFFFF
6440..6441 | L2N | 32 unsigned int (byte order: ABCD) | Line2-neutral voltage [0.1V] | 0xFFFFFFFF
6442..6443 | L3N | 32 unsigned int (byte order: ABCD) | Line3-neutral voltage [0.1V] | 0xFFFFFFFF
6444..6445 | L1A | 32 unsigned int (byte order: ABCD) | line1 current [mA] | 0xFFFFFFFF
6446..6447 | L2A | 32 unsigned int (byte order: ABCD) | line2 current [mA] | 0xFFFFFFFF
6448..6449 | L3A | 32 unsigned int (byte order: ABCD) | line3 current [mA] | 0xFFFFFFFF
6450..6451 | LNA | 32 unsigned int (byte order: ABCD) | Neutral current [mA] | 0xFFFFFFFF
6452..6453 | L1HZ | 32 unsigned int (byte order: ABCD) | Line1 frequency [0.01Hz] | 0xFFFFFFFF
6454..6455 | L2HZ | 32 unsigned int (byte order: ABCD) | Line2 frequency [0.01Hz] | 0xFFFFFFFF
6456..6457 | L3HZ | 32 unsigned int (byte order: ABCD) | Line1 frequency [0.01Hz] | 0xFFFFFFFF
6458..6459 | KWH_TOT | 32 unsigned int (byte order: ABCD) | Total energy [kWh] | 0xFFFFFFFF
6460..6461 | KWH_IMP | 32 unsigned int (byte order: ABCD) | Toatl energy imported [kWh] | 0xFFFFFFFF
6462..6463 | KWH_EXP | 32 unsigned int (byte order: ABCD) | Toatl energy exported [kWh] | 0xFFFFFFFF
6464..6465 | KVARH_TOT | 32 unsigned int (byte order: ABCD) | Total reactive energy [kVArh] | 0xFFFFFFFF
6466..6467 | KVARH_IND | 32 unsigned int (byte order: ABCD) | Total reactive inductive energy [kVArh] | 0xFFFFFFFF
6468..6469 | KVARH_CAP | 32 unsigned int (byte order: ABCD) | Total reactive capacitive energy [kVArh] | 0xFFFFFFFF
6470..6596 | RESERVED | Not defined | Reserved for later use | Not defined
6597 | DIG_STATUS | 16 unsigned int | Bitwise | Not defined
6598 | MB_POSITION | 16 unsigned int | 0: MB Off 1: MB On | Not defined
6599 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
Battery Power meter
Address | DataLabel | DataType | Description | Not available value
9600..9601 | ACP | 32 signed int (byte order: ABCD) | AC Power total [W] | 0x80000000
9602..9603 | ACQ | 32 signed int (byte order: ABCD) | AC Reactive power total [VAr] | 0x80000000
9604..9605 | ACS | 32 signed int (byte order: ABCD) | AC Apperant power total [VA] | 0x80000000
9606..9607 | PF | 32 signed int (byte order: ABCD) | Power factor total [0.001] | 0x80000000
9608..9609 | ACP1 | 32 signed int (byte order: ABCD) | AC Power line1 [W] | 0x80000000
9610..9611 | ACP2 | 32 signed int (byte order: ABCD) | AC Power line2 [W] | 0x80000000
9612..9613 | ACP3 | 32 signed int (byte order: ABCD) | AC Power line3 [W] | 0x80000000
9614..9615 | ACQ1 | 32 signed int (byte order: ABCD) | AC Reactive power line1 [VAr] | 0x80000000
9616..9617 | ACQ2 | 32 signed int (byte order: ABCD) | AC Reactive power line2 [VAr] | 0x80000000
9618..9619 | ACQ3 | 32 signed int (byte order: ABCD) | AC Reactive power line3 [VAr] | 0x80000000
9620..9621 | ACS1 | 32 signed int (byte order: ABCD) | AC Apperant power line1 [VA] | 0x80000000
9622..9623 | ACS2 | 32 signed int (byte order: ABCD) | AC Apperant power line2 [VA] | 0x80000000
9624..9625 | ACS3 | 32 signed int (byte order: ABCD) | AC Apperant power line3 [VA] | 0x80000000
9626..9627 | PF1 | 32 signed int (byte order: ABCD) | Power factor line1 [0.001] | 0x80000000
9628..9629 | PF2 | 32 signed int (byte order: ABCD) | Power factor line2 [0.001] | 0x80000000
9630..9631 | PF3 | 32 signed int (byte order: ABCD) | Power factor line3 [0.001] | 0x80000000
9632..9633 | L1L2 | 32 unsigned int (byte order: ABCD) | Line1-line2 voltage [0.1V] | 0xFFFFFFFF
9634..9635 | L2L3 | 32 unsigned int (byte order: ABCD) | Line2-line3 voltage [0.1V] | 0xFFFFFFFF
9636..9637 | L3L1 | 32 unsigned int (byte order: ABCD) | Line3-line1 voltage [0.1V] | 0xFFFFFFFF
9638..9639 | L1N | 32 unsigned int (byte order: ABCD) | Line1-neutral voltage [0.1V] | 0xFFFFFFFF
9640..9641 | L2N | 32 unsigned int (byte order: ABCD) | Line2-neutral voltage [0.1V] | 0xFFFFFFFF
9642..9643 | L3N | 32 unsigned int (byte order: ABCD) | Line3-neutral voltage [0.1V] | 0xFFFFFFFF
9644..9645 | L1A | 32 unsigned int (byte order: ABCD) | line1 current [mA] | 0xFFFFFFFF
9646..9647 | L2A | 32 unsigned int (byte order: ABCD) | line2 current [mA] | 0xFFFFFFFF
9648..9649 | L3A | 32 unsigned int (byte order: ABCD) | line3 current [mA] | 0xFFFFFFFF
9650..9651 | LNA | 32 unsigned int (byte order: ABCD) | Neutral current [mA] | 0xFFFFFFFF
9652..9653 | L1HZ | 32 unsigned int (byte order: ABCD) | Line1 frequency [0.01Hz] | 0xFFFFFFFF
9654..9655 | L2HZ | 32 unsigned int (byte order: ABCD) | Line2 frequency [0.01Hz] | 0xFFFFFFFF
9656..9657 | L3HZ | 32 unsigned int (byte order: ABCD) | Line1 frequency [0.01Hz] | 0xFFFFFFFF
9658..9659 | KWH_TOT | 32 unsigned int (byte order: ABCD) | Total energy [kWh] | 0xFFFFFFFF
9660..9661 | KWH_IMP | 32 unsigned int (byte order: ABCD) | Toatl energy imported [kWh] | 0xFFFFFFFF
9662..9663 | KWH_EXP | 32 unsigned int (byte order: ABCD) | Toatl energy exported [kWh] | 0xFFFFFFFF
9664..9665 | KVARH_TOT | 32 unsigned int (byte order: ABCD) | Total reactive energy [kVArh] | 0xFFFFFFFF
9666..9667 | KVARH_IND | 32 unsigned int (byte order: ABCD) | Total reactive inductive energy [kVArh] | 0xFFFFFFFF
9668..9669 | KVARH_CAP | 32 unsigned int (byte order: ABCD) | Total reactive capacitive energy [kVArh] | 0xFFFFFFFF
9670..9796 | RESERVED | Not defined | Reserved for later use | Not defined
9797 | DIG_STATUS | 16 unsigned int | Bitwise | Not defined
9798 | MB_POSITION | 16 unsigned int | 0: MB Off 1: MB On | Not defined
9799 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
PV Inverter number 1 to 32 The addressses of Inverter number x is found by: AddressInverter_x = (x-1) * 200 + Address
Address | DataLabel | DataType | Description | Not available value
10000..10015 | SN | Char, 32 byte Ascii characters | Serial number | Not defined
10016..10031 | MODEL | Char, 32 byte Ascii characters | Inverter model | Not defined
10032..10039 | VERSION | Char, 16 byte Ascii characters | Version | Not defined
10040..10099 | RESERVED | Not defined | Reserved for later use | Not defined
10100..10101 | ACP | 32 signed int (byte order: ABCD) | AC Power total [W] | 0x80000000
10102..10103 | ACQ | 32 signed int (byte order: ABCD) | AC Reactive power total [VAr] | 0x80000000
10104..10105 | ACS | 32 signed int (byte order: ABCD) | AC Apperant power total [VA] | 0x80000000
10106 | PF | 16 signed int | Power factor total [0.001] | 0x8000
10107 | L1N | 16 unsigned int | Line1-neutral voltage [0.1V] | 0xFFFF
10108 | L2N | 16 unsigned int | Line2-neutral voltage [0.1V] | 0xFFFF
10109 | L3N | 16 unsigned int | Line3-neutral voltage [0.1V] | 0xFFFF
10110 | L1L2 | 16 unsigned int | Line1-line2 voltage [0.1V] | 0xFFFF
10111 | L2L3 | 16 unsigned int | Line2-line3 voltage [0.1V] | 0xFFFF
10112 | L3L1 | 16 unsigned int | Line3-line1 voltage [0.1V] | 0xFFFF
10113 | RESERVED | Not defined | Reserved for later use | Not defined
10114 | L1A | 16 unsigned int | line1 current [0.1A] | 0xFFFF
10115 | L2A | 16 unsigned int | line2 current [0.1A] | 0xFFFF
10116 | L3A | 16 unsigned int | line3 current [0.1A] | 0xFFFF
10117 | HZ | 16 unsigned int | Grid frequency | 0xFFFF
10118 | DCA1 | 16 unsigned int | DC currrent input 1 [0.1A] | 0xFFFF
10119 | DCU1 | 16 unsigned int | DC voltage input 1 [0.1V] | 0xFFFF
10120 | DCP1 | 16 signed int | DC power input 1 [0.1kW] | 0x8000
10121 | DCA2 | 16 unsigned int | DC currrent input 2 [0.1A] | 0xFFFF
10122 | DCU2 | 16 unsigned int | DC voltage input 2 [0.1V] | 0xFFFF
10123 | DCP2 | 16 signed int | DC power input 2 [0.1kW] | 0x8000
10124 | DCA3 | 16 unsigned int | DC currrent input 3 [0.1A] | 0xFFFF
10125 | DCU3 | 16 unsigned int | DC voltage input 3 [0.1V] | 0xFFFF
10126 | DCP3 | 16 signed int | DC power input 3 [0.1kW] | 0x8000
10127 | DCA4 | 16 unsigned int | DC currrent input 4 [0.1A] | 0xFFFF
10128 | DCU4 | 16 unsigned int | DC voltage input 4 [0.1V] | 0xFFFF
10129 | DCP4 | 16 signed int | DC power input 4 [0.1kW] | 0x8000
10130..10131 | WH | 32 unsigned int (byte order: ABCD) | Energy total [kWh] | 0xFFFFFFFF
10132..10133 | WH_DAY | 32 unsigned int (byte order: ABCD) | Energy current day [0.1kWh] | 0xFFFFFFFF
10134..10135 | HOURS | 32 unsigned int (byte order: ABCD) | Operation time total [hours] | 0xFFFFFFFF
10136 | MIN_DAY | 16 unsigned int | Operation time current day [minuttes] | 0xFFFF
10137 | CAB_TEMP | 16 signed int | Cabinet temperature [0.1C] | 0x8000
10138 | STATE | 16 unsigned int | Inverter state | 0xFFFF
10139..10140 | EVT1 | 32 unsigned int (byte order: ABCD) | Event field 1 | 0xFFFFFFFF
10141..10142 | EVT2 | 32 unsigned int (byte order: ABCD) | Event field 2 | 0xFFFFFFFF
10143..10144 | EVT3 | 32 unsigned int (byte order: ABCD) | Event field 3 | 0xFFFFFFFF
10145..10146 | EVT4 | 32 unsigned int (byte order: ABCD) | Event field 4 | 0xFFFFFFFF
10147..10198 | RESERVED | Not defined | Reserved for later use | Not defined
10199 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
Sensor number 1 to 4 The addressses of Sensor number x is found by: AddressSensor_x = (x-1) * 20 + Address
Address | DataLabel | DataType | Description | Not available value
20000 | POA | 16 unsigned int | Plane of Aray irradiance [W/m2] | 0xFFFF
20001 | BOM | 16 signed int | Back of module temperature [0.1C] | 0x8000
20002 | GHI | 16 unsigned int | Global horizontal irradiance [W/m2] | 0xFFFF
20003 | AMB_TEMP | 16 signed int | Ambient temperature [0.1C] | 0x8000
20004 | WIND_SPEED | 16 unsigned int | Wind speed [m/s] | 0xFFFF
20005 | REL_HUMIDITY | 16 signed int | Relative humidity [%] | 0x8000
20006 | BAR_PRES | 16 signed int | Barometrical pressure [HPa] | 0x8000
20007 | WIND_DIR | 16 signed int | Wind direction [deg] | 0x8000
20008 | RAIN | 16 signed int | Rain fall [mm] | 0x8000
20009 | FUEL_LEVEL | 16 signed int | Fuel level [0.1%] | 0x8000
20010 | FUEL_PRESSURE | 16 signed int | Fuel pressure [mbar] | 0x8000
20011..20018 | RESERVED | Not defined | Reserved for later use | Not defined
20019 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
IO module number 1 to 4 The addressses of module number x is found by: AddressModule_x = (x-1) * 50 + Address
Address | DataLabel | DataType | Description | Not available value
20500 | INPUT_1_16 | 16 unsigned int | bitwise | Not defined
20501 | OUTPUT_1_16 | 16 unsigned int | bitwise | Not defined
20502..20503 | AIO_INPUT_01 | FLOAT (byte order: ABCD) | Analogue input 01 | Not defined
20504..20505 | AIO_INPUT_02 | FLOAT (byte order: ABCD) | Analogue input 02 | Not defined
20506..20507 | AIO_INPUT_03 | FLOAT (byte order: ABCD) | Analogue input 03 | Not defined
20508-20509 | AIO_INPUT_04 | FLOAT (byte order: ABCD) | Analogue input 04 | Not defined
20510..20511 | AIO_INPUT_05 | FLOAT (byte order: ABCD) | Analogue input 05 | Not defined
20512..20513 | AIO_INPUT_06 | FLOAT (byte order: ABCD) | Analogue input 06 | Not defined
20514..20515 | AIO_INPUT_07 | FLOAT (byte order: ABCD) | Analogue input 07 | Not defined
20516..20517 | AIO_INPUT_08 | FLOAT (byte order: ABCD) | Analogue input 08 | Not defined
20518..20519 | AIO_OUTPUT_01 | FLOAT (byte order: ABCD) | Analogue output 01 | Not defined
20520..20521 | AIO_OUTPUT_02 | FLOAT (byte order: ABCD) | Analogue output 02 | Not defined
20522..20523 | AIO_OUTPUT_03 | FLOAT (byte order: ABCD) | Analogue output 03 | Not defined
20524..20525 | AIO_OUTPUT_04 | FLOAT (byte order: ABCD) | Analogue output 04 | Not defined
20526..20527 | AIO_OUTPUT_05 | FLOAT (byte order: ABCD) | Analogue output 05 | Not defined
20528..20529 | AIO_OUTPUT_06 | FLOAT (byte order: ABCD) | Analogue output 06 | Not defined
20530..20531 | AIO_OUTPUT_07 | FLOAT (byte order: ABCD) | Analogue output 07 | Not defined
20532..20533 | AIO_OUTPUT_08 | FLOAT (byte order: ABCD) | Analogue output 08 | Not defined
20534 | CH_CONF_01 | 16 unsigned int | Channel confirguration 01 | Not defined
20535 | CH_CONF_02 | 16 unsigned int | Channel confirguration 02 | Not defined
20536 | CH_CONF_03 | 16 unsigned int | Channel confirguration 03 | Not defined
20537 | CH_CONF_04 | 16 unsigned int | Channel confirguration 04 | Not defined
20538 | CH_CONF_05 | 16 unsigned int | Channel confirguration 05 | Not defined
20539 | CH_CONF_06 | 16 unsigned int | Channel confirguration 06 | Not defined
20540 | CH_CONF_07 | 16 unsigned int | Channel confirguration 07 | Not defined
20541 | CH_CONF_08 | 16 unsigned int | Channel confirguration 08 | Not defined
20542 | CH_STATUS | 16 unsigned int | Channel status | Not defined
20543 | MOD_TEMP | 16 unsigned int | Module temperature [0.1C] | Not defined
20544..20548 | RESERVED | Not defined | Reserved for later use | Not defined
20549 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
CONFIGURABLE MODBUS AREA
20900..20947 | CONF_MODBUS_AREA_ADDR_0_47 | Not defined | Data mapped from the rest of the starndard modbus map (fcn 0x04) | Not defined
Battery inverter Acquisition
Address | DataLabel | DataType | Description | Not available value
21000 | SN | Char, 32 byte Ascii characters | Serial number | Not defined
21016..21031 | MODEL | Char, 32 byte Ascii characters | Inverter model | Not defined
21032..21039 | VERSION | Char, 16 byte Ascii characters | Version | Not defined
21040..21099 | RESERVED | Not defined | Reserved for later use | Not defined
21100..21101 | ACP | 32 signed int (byte order: ABCD) | AC Power total [W] | 0x80000000
21102..21103 | ACP L1 | 32 signed int (byte order: ABCD) | AC Power line1 [W] | 0x80000000
21104..21105 | ACP L2 | 32 signed int (byte order: ABCD) | AC Power line2 [W] | 0x80000000
21106..21107 | ACP L3 | 32 signed int (byte order: ABCD) | AC Power line3 [W] | 0x80000000
21108..21109 | ACQ | 32 signed int (byte order: ABCD) | AC Reactive power total [VAr] | 0x80000000
21110..21111 | ACQ L1 | 32 signed int (byte order: ABCD) | AC Reactive power line1 [VAr] | 0x80000000
21112..21113 | ACQ L2 | 32 signed int (byte order: ABCD) | AC Reactive power line2 [VAr] | 0x80000000
21114..21115 | ACQ L3 | 32 signed int (byte order: ABCD) | AC Reactive power line3 [VAr] | 0x80000000
21116..21117 | ACS | 32 signed int (byte order: ABCD) | AC Apperant power total [VA] | 0x80000000
21118..21119 | ACS L1 | 32 signed int (byte order: ABCD) | AC Apparent power line1 [VA] | 0x80000000
21120..21121 | ACS L2 | 32 signed int (byte order: ABCD) | AC Apparent power line2 [VA] | 0x80000000
21122..21123 | ACS L3 | 32 signed int (byte order: ABCD) | AC Apparent power line3 [VA] | 0x80000000
21124 | PF | 16 signed int | Power factor total [0.001] | 0x8000
21125 | PF L1 | 16 signed int | Power factor line1 [0.001] | 0x8000
21126 | PF L2 | 16 signed int | Power factor line2 [0.001] | 0x8000
21127 | PF L3 | 16 signed int | Power factor line3 [0.001] | 0x8000
21128..21129 | WH | 32 unsigned int (byte order: ABCD) | Energy total [kWh] | 0xFFFFFFFF
21130..21131 | WH_IMP | 32 unsigned int (byte order: ABCD) | Energy total import [0.1kWh] | 0xFFFFFFFF
21132 | L1N | 16 unsigned int | Line1-neutral voltage [0.1V] | 0xFFFF
21133 | L2N | 16 unsigned int | Line2-neutral voltage [0.1V] | 0xFFFF
21134 | L3N | 16 unsigned int | Line3-neutral voltage [0.1V] | 0xFFFF
21135 | L1L2 | 16 unsigned int | Line1-line2 voltage [0.1V] | 0xFFFF
21136 | L2L3 | 16 unsigned int | Line2-line3 voltage [0.1V] | 0xFFFF
21137 | L3L1 | 16 unsigned int | Line3-line1 voltage [0.1V] | 0xFFFF
21138 | L1A | 16 signed int | line1 current [0.1A] | 0x8000
21139 | L2A | 16 signed int | line2 current [0.1A] | 0x8000
21140 | L3A | 16 signed int | line3 current [0.1A] | 0x8000
21141 | LNA | 16 signed int | Neutral current [0.1A] | 0x8000
21142 | FL1 | 16 unsigned int | L1 frequency [0.01Hz] | 0xFFFF
21143 | FL2 | 16 unsigned int | L2 frequency [0.01Hz] | 0xFFFF
21144 | FL3 | 16 unsigned int | L3 frequency [0.01Hz] | 0xFFFF
21145 | CAB_TEMP | 16 signed int | Cabinet temperature [0.1C] | 0x8000
21146 | STATE | 16 unsigned int | Inverter state | 0xFFFF
21147 | DCA1 | 16 signed int | DC currrent input 1 [0.1A] | 0xFFFF
21148 | DCU1 | 16 unsigned int | DC voltage input 1 [0.1V] | 0xFFFF
21149 | DCP1 | 16 signed int | DC power input 1 [0.1kW] | 0x8000
21150 | DCA2 | 16 signed int | DC currrent input 2 [0.1A] | 0xFFFF
21151 | DCU2 | 16 unsigned int | DC voltage input 2 [0.1V] | 0xFFFF
21152 | DCP2 | 16 signed int | DC power input 2 [0.1kW] | 0x8000
21153..21154 | EVT1 | 32 unsigned int (byte order: ABCD) | Event field 1 | 0xFFFFFFFF
21155..21156 | EVT2 | 32 unsigned int (byte order: ABCD) | Event field 2 | 0xFFFFFFFF
21157..21158 | EVT3 | 32 unsigned int (byte order: ABCD) | Event field 3 | 0xFFFFFFFF
21159..21160 | EVT4 | 32 unsigned int (byte order: ABCD) | Event field 4 | 0xFFFFFFFF
21161 | SOC | 16 unsigned int | State of charge [0.1%] | 0xFFFF
21162..21163 | SOE | 32 unsigned int (byte order: ABCD) | State of energy [0.1kWh] | 0xFFFFFFFF
21164 | SOH | 16 unsigned int | State of health [0.1%] | 0xFFFF
21165..21166 | OCC | 32 unsigned int (byte order: ABCD) | Online charging capacity [0.1kW] | 0xFFFFFFFF
21167..21168 | OGC | 32 unsigned int (byte order: ABCD) | Online discharging capacity [0.1kW] | 0xFFFFFFFF
21169 | MIN CELL VOLTAGE | 16 unsigned int | Minimum cell voltage [mV] | 0xFFFF
21170 | MAX CELL VOLTAGE | 16 unsigned int | Maximum cell voltage [mV] | 0xFFFF
21171 | MIN CELL TEMPERATURE | 16 signed int | Minimum temperature voltage [0.1C] | 0x8000
21172 | MAX CELL TEMPERATURE | 16 signed int | Maximum temperature voltage [0.1C] | 0x8000
21173 | BMS_STATE | 16 unsigned int | BMS state | 0xFFFF
21174 | RESERVED | Not defined | Reserved for later use | Not defined
21175 | MIN_CELL_V_CHANEL | 16 unsigned int | Minimum cell voltage channel | 0xFFFF
21176 | MAX_CELL_V_CHANEL | 16 signed int | Maximum cell voltage channel | 0xFFFF
21177 | MIN_CELL_T_CHANEL | 16 unsigned int | Minimum cell temperature channel | 0xFFFF
21178 | MAX_CELL_T_CHANEL | 16 signed int | Maximum cell temperature channel | 0xFFFF
21179..21198 | RESERVED | Not defined | Reserved for later use | Not defined
21199 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
Grid support - frequency
22200..22201 | GRIDSUPPORT_FREQ | FLOAT (byte order: ABCD) | Grid frequency [Hz] | Not defined
22202..22203 | GRIDSUPPORT_P | FLOAT (byte order: ABCD) | PV power [kW] | Not defined
22204..22205 | GRIDSUPPORT_P_BAT | FLOAT (byte order: ABCD) | Battery power [kW] | Not defined
22206..22207 | GRIDSUPPORT_P_PCT | FLOAT (byte order: ABCD) | PV power percentage of installed inverter capacity [%] | Not defined
22208..22209 | GRIDSUPPORT_P_BAT_PCT | FLOAT (byte order: ABCD) | Battery power percentage of installed PCS capacity [%] | Not defined
22210..22211 | GRIDSUPPORT_PF_P_COMP | FLOAT (byte order: ABCD) | PV total P(f) compensation [kW] | Not defined
22212..22213 | GRIDSUPPORT_PF_P_BAT_COMP | FLOAT (byte order: ABCD) | Battery total P(f) compensation [kW] | Not defined
22214..22215 | GRIDSUPPORT_PF01_F_COMP | FLOAT (byte order: ABCD) | Frequency compensation from P(f) PV [Hz] | Not defined
22216..22217 | GRIDSUPPORT_PF01_TRIGGER_P | FLOAT (byte order: ABCD) | PV trigger power P(f) PV [kW] | Not defined
22218..22219 | GRIDSUPPORT_PF01_P_COMP | FLOAT (byte order: ABCD) | PV compensation power P(f) PV [kW] | Not defined
22220..22221 | GRIDSUPPORT_PF02_F_COMP | FLOAT (byte order: ABCD) | Frequency compensation from P(f) Battery [Hz] | Not defined
22222..22223 | GRIDSUPPORT_PF02_TRIGGER_P | FLOAT (byte order: ABCD) | PV trigger power P(f) Battery [kW] | Not defined
22224..22225 | GRIDSUPPORT_PF02_P_COMP | FLOAT (byte order: ABCD) | PV compensation power P(f) Battery [kW] | Not defined
22226..22299 | Reserved | Not defined | Reserved for later use | Not defined
Grid support - voltage
22300..22301 | GRIDSUPPORT_VOLT | FLOAT (byte order: ABCD) | Grid voltage [V] | Not defined
22302..22303 | GRIDSUPPORT_Q | FLOAT (byte order: ABCD) | PV reactive power [kVAr] | Not defined
22304..22305 | GRIDSUPPORT_Q_BAT | FLOAT (byte order: ABCD) | Battery reactive power [kVAr] | Not defined
22306..22307 | GRIDSUPPORT_Q_PCT | FLOAT (byte order: ABCD) | PV reactive power percentage of installed inverter capacity [%] | Not defined
22308..22309 | GRIDSUPPORT_Q_BAT_PCT | FLOAT (byte order: ABCD) | Battery reactive power percentage of installed PCS capacity [%] | Not defined
22310..22311 | GRIDSUPPORT_QU_Q_COMP | FLOAT (byte order: ABCD) | PV total Q(U) compensation [kVAr] | Not defined
22312..22313 | GRIDSUPPORT_QU_Q_BAT_COMP | FLOAT (byte order: ABCD) | Battery total Q(U) compensation [kVAr] | Not defined
22314..22315 | GRIDSUPPORT_QU01_F_COMP | FLOAT (byte order: ABCD) | Voltage compensation from Q(U) PV [V] | Not defined
22316..22317 | GRIDSUPPORT_QU01_TRIGGER_P | FLOAT (byte order: ABCD) | PV trigger reactive power Q(U) PV [kVAr] | Not defined
22318..22319 | GRIDSUPPORT_QU01_P_COMP | FLOAT (byte order: ABCD) | PV compensation reactive power Q(U) PV [kVAr] | Not defined
22320..22321 | GRIDSUPPORT_QU02_F_COMP | FLOAT (byte order: ABCD) | Voltage compensation from Q(U) Battery [V] | Not defined
22322..22323 | GRIDSUPPORT_QU02_TRIGGER_P | FLOAT (byte order: ABCD) | PV trigger reactive power Q(U) battery [kVAr] | Not defined
22324..22325 | GRIDSUPPORT_QU02_P_COMP | FLOAT (byte order: ABCD) | PV compensation reactive power Q(U) Battery [kVAr] | Not defined
22326..22399 | Reserved | Not defined | Reserved for later use | Not defined
BMS Acquisition
Address | DataLabel | DataType | Description | Not available value
25000 | SN | Char, 32 byte Ascii characters | Serial number | Not defined
25016..25031 | MODEL | Char, 32 byte Ascii characters | Inverter model | Not defined
25032..25039 | VERSION | Char, 16 byte Ascii characters | Version | Not defined
25040..25099 | RESERVED | Not defined | Reserved for later use | Not defined
25100 | BMS_STATE | 16 unsigned int | BMS state | 0xFFFF
25101 | SOC | 16 unsigned int | State of charge [0.1%] | 0xFFFF
25102..25103 | SOE | 32 unsigned int (byte order: ABCD) | State of energy [0.1kWh] | 0xFFFFFFFF
25104 | SOH | 16 unsigned int | State of health [0.1%] | 0xFFFF
25105 | MAX_CHARGE_VOLT | 16 unsigned int | Maximum charge voltage [0.1V] | 0xFFFF
25106 | MAX_CHARGE_CURRENT | 16 signed int | Maximum charge current [0.1A] | 0x8000
25107..25108 | OCC | 32 unsigned int (byte order: ABCD) | Online charging capacity [0.1kW] | 0xFFFFFFFF
25109 | MAX_DISCHARGE_VOLT | 16 unsigned int | Maximum discharge voltage [0.1V] | 0xFFFF
25110 | MAX_DISCHARGE_CURRENT | 16 signed int | Maximum discharge current [0.1A] | 0x8000
25111..25112 | ODC | 32 unsigned int (byte order: ABCD) | Online charging capacity [0.1kW] | 0xFFFFFFFF
25113 | MIN_CELL_V | 16 unsigned int | Minimum cell voltage [mV] | 0xFFFF
25114 | MAX_CELL_V | 16 unsigned int | Maximum cell voltage [mV] | 0xFFFF
25115 | MIN_CELL_V_CHANEL | 16 unsigned int | Minimum cell voltage channel | 0xFFFF
25116 | MAX_CELL_V_CHANEL | 16 signed int | Maximum cell voltage channel | 0xFFFF
25117 | MIN_CELL_T | 16 signed int | Minimum temperature [0.1C] | 0x8000
25118 | MAX_CELL_T | 16 signed int | Maximum temperature [0.1C] | 0x8000
25119 | MIN_CELL_T_CHANEL | 16 unsigned int | Minimum cell temperature channel | 0xFFFF
25120 | MAX_CELL_T_CHANEL | 16 signed int | Maximum cell temperature channel | 0xFFFF
25121 | MIN_MODULE_V | 16 unsigned int | Minimum cell voltage [0.1V] | 0xFFFF
25122 | MAX_MODULE_V | 16 unsigned int | Maximum cell voltage [0.1V] | 0xFFFF
25123 | MIN_MODULE_V_CHANEL | 16 unsigned int | Minimum cell voltage channel | 0xFFFF
25124 | MAX_MODULE_V_CHANEL | 16 signed int | Maximum cell voltage channel | 0xFFFF
25125 | MIN_MODULE_T | 16 signed int | Minimum temperature [0.1C] | 0x8000
25126 | MAX_MODULE_T | 16 signed int | Maximum temperature [0.1C] | 0x8000
25127 | MIN_MODULE_T_CHANEL | 16 unsigned int | Minimum cell temperature channel | 0xFFFF
25128 | MAX_MODULE_T_CHANEL | 16 signed int | Maximum cell temperature channel | 0xFFFF
25129 | NBR_PILES | 16 unsigned int | Number of module piles/stacks | 0xFFFF
25130 | NBR_MODULES_IN_PILE | 16 unsigned int | Number of modules in each pile/stack | 0xFFFF
25131 | DCA | 16 signed int | DC current input [0.1A] | 0x8000
25132 | DCU | 16 unsigned int | DC voltage input [0.1V] | 0xFFFF
25133 | DCP | 16 unsigned int | DC power input [0.1kW] | 0x8000
25134..25135 | EVT1 | 32 unsigned int (byte order: ABCD) | Event field 1 | 0xFFFFFFFF
25136..25137 | EVT2 | 32 unsigned int (byte order: ABCD) | Event field 2 | 0xFFFFFFFF
25138..25139 | EVT3 | 32 unsigned int (byte order: ABCD) | Event field 3 | 0xFFFFFFFF
25140..25141 | EVT4 | 32 unsigned int (byte order: ABCD) | Event field 4 | 0xFFFFFFFF
25142 | TEMP | 16 signed int | Temperature [0.1C] | 0x8000
25143..25198 | RESERVED | Not defined | Reserved for later use | Not defined
25199 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
HVAC Acquisition
Address | DataLabel | DataType | Description | Not available value
26000..26015 | SN | Char, 32 byte Ascii characters | Serial number | Not defined
26016..26031 | MODEL | Char, 32 byte Ascii characters | Inverter model | Not defined
26032..26039 | VERSION | Char, 16 byte Ascii characters | Version | Not defined
26040..26099 | RESERVED | Not defined | Reserved for later use | Not defined
26100 | HVAC_STATE | 16 unsigned int | HVAC state | 0xFFFF
26101 | RETURN_TEMP | 16 signed int | Return temperature [0.1C] | 0x8000
26102 | RETURN_HUMIDITY | 16 unsigned int | Return humidity [0.1%] | 0xFFFF
26103 | INT_FAN_SPEED | 16 unsigned int | Internal fan speed [rpm] | 0xFFFF
26104 | EXT_FAN_SPEED | 16 unsigned int | External fan speed [rpm] | 0xFFFF
26105 | INT_FAN_ON | 16 unsigned int | Internal fan ON status | 0xFFFF
26106 | EXT_FAN_ON | 16 unsigned int | External fan ON status | 0xFFFF
26107 | COOLING_ON | 16 unsigned int | Cooling ON status | 0xFFFF
26108 | HEATING_ON | 16 unsigned int | Heating ON status | 0xFFFF
26109 | SENSOR_FAULT | 16 unsigned int | Sensor fault | 0xFFFF
26110 | HIGH_VOLT_ALARM | 16 unsigned int | High voltage alarm | 0xFFFF
26111 | TEMP_ALARM | 16 unsigned int | Temperature alarm | 0xFFFF
26112 | PRES_ALARM | 16 unsigned int | Pressure alarm | 0xFFFF
26113 | COMPRESSOR_FAULT | 16 unsigned int | Compressor fault | 0xFFFF
26114 | HEATER_FAULT | 16 unsigned int | Heater fault | 0xFFFF
26115 | INT_FAN_ALARM | 16 unsigned int | Internal fan alarm | 0xFFFF
26116 | EXT_FAN_ALARM | 16 unsigned int | External fan alarm | 0xFFFF
26117 | INSIDE_TEMP | 16 signed int | Inside temperature [0.1C] | 0x8000
26118 | OUTSIDE_TEMP | 16 signed int | Outside temperature [0.1C] | 0x8000
26119..26198 | RESERVED | Not defined | Reserved for later use | Not defined
26199 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
COMMAND PANEL TEXTS
27000..27079 | TEXT_CMD_PANEL_BUTTON 01..04 | string | User configurable texts for command panel button 01..04 | Not defined
27080..27159 | TEXT_CMD_PANEL_BUTTON 05..08 | string | User configurable texts for command panel button 05..08 | Not defined
27160..27239 | TEXT_CMD_PANEL_BUTTON 09..12 | string | User configurable texts for command panel button 09..12 | Not defined
27240..27319 | TEXT_CMD_PANEL_BUTTON 13..16 | string | User configurable texts for command panel button 13..16 | Not defined
27320..27399 | TEXT_CMD_PANEL_LED 01..04 | string | User configurable texts for command panel led 01..04 | Not defined
27400..27479 | TEXT_CMD_PANEL_LED 05..08 | string | User configurable texts for command panel led 05..08 | Not defined
27480..27559 | TEXT_CMD_PANEL_LED 09..12 | string | User configurable texts for command panel led 09..12 | Not defined
27560..27639 | TEXT_CMD_PANEL_LED 13..16 | string | User configurable texts for command panel led 13..16 | Not defined
27640..27999 | RESERVED | Not defined | Reserved for later use | Not defined
ECLOGIC BUILDER AREA 1
28000 | Q1 gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28001 | Q2 gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28002 | Q3 gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28003 | Q-out gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28004 | Inverted Q-out gate output status line 1-16 | 16 unsigned int | bitwise | Not defined
28005..28099 | RESERVED | Not defined | Reserved for later use | Not defined
SPOTPRICE AREA
28100 | SPOTPRICE_BIT_STATUS | 16 unsigned int | BIT0: Spotprices valid BIT1: Spotprice negative BIT2: Import price negative BIT3: Export price negative | Not defined
28101..28148 | SPOTPRICES_CURRENCY_KWH | FLOAT (byte order: ABCD) | Todays hourly spotprices [00..23] from the selected market [currency/kWh] | Not defined
28149..28150 | SPOTPRICE_IMPORT_CURRENCY_KWH | FLOAT (byte order: ABCD) | Instant spot price including import tariff [currency/kWh] | Not defined
28151..28152 | SPOTPRICE_EXPORT_CURRENCY_KWH | FLOAT (byte order: ABCD) | Instant spot price including export tariff [currency/kWh] | Not defined
28153..28200 | SPOTPRICE_IMPORT_TARIFF | FLOAT (byte order: ABCD) | Todays hourly import tariffs [00..23] from the selected market [currency/kWh] | Not defined
28201..28248 | SPOTPRICE_EXPORT_TARIFF | FLOAT (byte order: ABCD) | Todays hourly export tariffs [00..23] from the selected market [currency/kWh] | Not defined
28249..28499 | RESERVED | Not defined | Reserved for later use | Not defined
OPTIMIZER AREA
28500 | OPTIMIZER_BIT_STATUS | 16 unsigned int | BIT0: optimizer chart valid | Not defined
28501..28524 | CHARGE/DISCHARGE ACTION | 16 signed int | Todays hourly SOC charge/discharge action [00..23] [%] | Not defined
28525..28548 | SOC PROFILE | 16 signed int | Todays hourly SOC profile action [00..23] [%] | Not defined
28549..28596 | PROFIT PROFILE | FLOAT (byte order: ABCD) | Todays hourly profit [00..23] [Euro] | Not defined
28597..28598 | PROFIT_TOTAL | FLOAT (byte order: ABCD) | Todays expected profit [Euro] | Not defined
28599..28600 | ENERGY_CHARGED | FLOAT (byte order: ABCD) | Todays expected amount of energy charged [kWh] | Not defined
28601..28602 | ENERGY_DISCHARGED | FLOAT (byte order: ABCD) | Todays expected amount of energy discharged [kWh] | Not defined
28603..28604 | ENERGY_TOTAL | FLOAT (byte order: ABCD) | Todays expected amount of energy troughput [kWh] | Not defined
28605..28606 | PROFIT_ACTUAL | FLOAT (byte order: ABCD) | Todays actual profit [Euro] | Not defined
28607..28630 | CHARGE_DISCHARGE_ACTION_TYPE | 16 unsigned int | Todays hourly charge action type [00..23] | Not defined
28631..28654 | BAT_KWH_PROFILE | 16 signed int | Todays expected hourly battery energy profile [00..23] [kWh] | Not defined
28655..28678 | GRID_KWH_PROFILE | 16 signed int | Todays expected hourly mains energy profile [00..23] [kWh] | Not defined
28679..28702 | CONSUMPTION_KWH | 16 signed int | Todays expected hourly consumption [00..23] [kWh] | Not defined
28703..28726 | PV_AVAILABLE_KWH | 16 signed int | Todays expected available PV energy [00..23] [kWh] | Not defined
28727..28750 | PV_AC_AVAILABLE_KWH | 16 signed int | Todays expected available AC PV energy [00..23] [kWh] | Not defined
28751..28774 | PV_AC_PRODUCED_KWH | 16 signed int | Todays expected AC PV energy production [00..23] [kWh] | Not defined
28775..28798 | PV_DC_AVAILABLE_KWH | 16 signed int | Todays expected available DC PV energy [00..23] [kWh] | Not defined
28799..28822 | PV_DC_PRODUCED_KWH | 16 signed int | Todays expected DC PV energy production [00..23] [kWh] | Not defined
28823..28824 | CONSUMPTION_KWH_TOTAL | 32 signed int (byte order: ABCD) | Todays expected total consumption [kWh] | Not defined
28825..28826 | PV_AVAILABLE_KWH_TOTAL | 32 signed int (byte order: ABCD) | Todays expected total available PV energy [kWh] | Not defined
28827..28828 | PV_AC_AVAILABLE_KWH_TOTAL | 32 signed int (byte order: ABCD) | Todays expected total available AC PV energy [kWh] | Not defined
28829..28830 | PV_AC_PRODUCED_KWH_TOTAL | 32 signed int (byte order: ABCD) | Todays expected total AC PV energy prodcution [kWh] | Not defined
28831..28832 | PV_DC_AVAILABLE_KWH_TOTAL | 32 signed int (byte order: ABCD) | Todays expected total available DC PV energy [kWh] | Not defined
28833..28834 | PV_DC_PRODUCED_KWH_TOTAL | 32 signed int (byte order: ABCD) | Todays expected total DC PV energy production [kWh] | Not defined
28835..28999 | RESERVED | Not defined | Reserved for later use | Not defined
ECLOGIC LINKER COMMAND AREA 1
29000 | GB_POSITION 1-16 | 16 unsigned int | bitwise | Not defined
29001 | MB_POSITION 1-16 | 16 unsigned int | bitwise | Not defined
29002 | Relay 1-16 on all DG meters | 16 unsigned int | bitwise | Not defined
29003 | Relay 1-16 on DG meter 1 | 16 unsigned int | bitwise | Not defined
29004 | Relay 1-16 on DG meter 2 | 16 unsigned int | bitwise | Not defined
29005 | Relay 1-16 on DG meter 3 | 16 unsigned int | bitwise | Not defined
29006 | Relay 1-16 on DG meter 4 | 16 unsigned int | bitwise | Not defined
29007 | Relay 1-16 on DG meter 5 | 16 unsigned int | bitwise | Not defined
29008 | Relay 1-16 on DG meter 6 | 16 unsigned int | bitwise | Not defined
29009 | Relay 1-16 on DG meter 7 | 16 unsigned int | bitwise | Not defined
29010 | Relay 1-16 on DG meter 8 | 16 unsigned int | bitwise | Not defined
29011 | Relay 1-16 on DG meter 9 | 16 unsigned int | bitwise | Not defined
29012 | Relay 1-16 on DG meter 10 | 16 unsigned int | bitwise | Not defined
29013 | Relay 1-16 on DG meter 11 | 16 unsigned int | bitwise | Not defined
29014 | Relay 1-16 on DG meter 12 | 16 unsigned int | bitwise | Not defined
29015 | Relay 1-16 on DG meter 13 | 16 unsigned int | bitwise | Not defined
29016 | Relay 1-16 on DG meter 14 | 16 unsigned int | bitwise | Not defined
29017 | Relay 1-16 on DG meter 15 | 16 unsigned int | bitwise | Not defined
29018 | Relay 1-16 on DG meter 16 | 16 unsigned int | bitwise | Not defined
29019 | Relay 1-16 on all PV meters | 16 unsigned int | bitwise | Not defined
29020 | Relay 1-16 on PV meter 1 | 16 unsigned int | bitwise | Not defined
29021 | Relay 1-16 on PV meter 2 | 16 unsigned int | bitwise | Not defined
29022 | Relay 1-16 on PV meter 3 | 16 unsigned int | bitwise | Not defined
29023 | Relay 1-16 on PV meter 4 | 16 unsigned int | bitwise | Not defined
29024 | Relay 1-16 on PV meter 5 | 16 unsigned int | bitwise | Not defined
29025 | Relay 1-16 on PV meter 6 | 16 unsigned int | bitwise | Not defined
29026 | Relay 1-16 on PV meter 7 | 16 unsigned int | bitwise | Not defined
29027 | Relay 1-16 on PV meter 8 | 16 unsigned int | bitwise | Not defined
29028 | Relay 1-16 on PV meter 9 | 16 unsigned int | bitwise | Not defined
29029 | Relay 1-16 on PV meter 10 | 16 unsigned int | bitwise | Not defined
29030 | Relay 1-16 on PV meter 11 | 16 unsigned int | bitwise | Not defined
29031 | Relay 1-16 on PV meter 12 | 16 unsigned int | bitwise | Not defined
29032 | Relay 1-16 on PV meter 13 | 16 unsigned int | bitwise | Not defined
29033 | Relay 1-16 on PV meter 14 | 16 unsigned int | bitwise | Not defined
29034 | Relay 1-16 on PV meter 15 | 16 unsigned int | bitwise | Not defined
29035 | Relay 1-16 on PV meter 16 | 16 unsigned int | bitwise | Not defined
29036 | Relay 1-16 on all Mains meters | 16 unsigned int | bitwise | Not defined
29037 | Relay 1-16 on Mains meter 1 | 16 unsigned int | bitwise | Not defined
29038 | Relay 1-16 on Mains meter 2 | 16 unsigned int | bitwise | Not defined
29039 | Relay 1-16 on Mains meter 3 | 16 unsigned int | bitwise | Not defined
29040 | Relay 1-16 on Mains meter 4 | 16 unsigned int | bitwise | Not defined
29041 | Relay 1-16 on Mains meter 5 | 16 unsigned int | bitwise | Not defined
29042 | Relay 1-16 on Mains meter 6 | 16 unsigned int | bitwise | Not defined
29043 | Relay 1-16 on Mains meter 7 | 16 unsigned int | bitwise | Not defined
29044 | Relay 1-16 on Mains meter 8 | 16 unsigned int | bitwise | Not defined
29045 | Relay 1-16 on Mains meter 9 | 16 unsigned int | bitwise | Not defined
29046 | Relay 1-16 on Mains meter 10 | 16 unsigned int | bitwise | Not defined
29047 | Relay 1-16 on Mains meter 11 | 16 unsigned int | bitwise | Not defined
29048 | Relay 1-16 on Mains meter 12 | 16 unsigned int | bitwise | Not defined
29049 | Relay 1-16 on Mains meter 13 | 16 unsigned int | bitwise | Not defined
29050 | Relay 1-16 on Mains meter 14 | 16 unsigned int | bitwise | Not defined
29051 | Relay 1-16 on Mains meter 15 | 16 unsigned int | bitwise | Not defined
29052 | Relay 1-16 on Mains meter 16 | 16 unsigned int | bitwise | Not defined
29053 | Mimimum genset load 1-8 | 16 unsigned int | bitwise | Not defined
29054 | Genset1 rated power 1-8 | 16 unsigned int | bitwise | Not defined
29055 | RRCR input 1-4 | 16 unsigned int | bitwise | Not defined
29056 | Relay 1-16 on all IO modules | 16 unsigned int | bitwise | Not defined
29057 | Relay 1-16 on IO module 1 | 16 unsigned int | bitwise | Not defined
29058 | Relay 1-16 on IO module 2 | 16 unsigned int | bitwise | Not defined
29059 | Relay 1-16 on IO module 3 | 16 unsigned int | bitwise | Not defined
29060 | Relay 1-16 on IO module 4 | 16 unsigned int | bitwise | Not defined
29061 | SOC Set flip flop 1-8 | 16 unsigned int | bitwise | Not defined
29062 | SOC Reset flip flop 1-8 | 16 unsigned int | bitwise | Not defined
29063 | Synchronize Mains breaker | 16 unsigned int | bitwise | Not defined
29064 | Deload Mains breaker | 16 unsigned int | bitwise | Not defined
29065 | AIO RRCR input | 16 unsigned int | bitwise | Not defined
29066 | Cmd panel LED 01..16: Green | 16 unsigned int | bitwise | Not defined
29067 | Cmd panel LED 01..16: Red | 16 unsigned int | bitwise | Not defined
29068 | EClogic Alarms 01..08 | 16 unsigned int | bitwise | Not defined
29069 | EClogic Timers 01..08 | 16 unsigned int | bitwise | Not defined
29070 | Deload battery | 16 unsigned int | BIT0 Low: Off BIT0 High: On | Not defined
29071 | Activate Genset Mode | 16 unsigned int | BIT0 Low: Off BIT0 High: On | Not defined
29072 | Dectivate Genset Mode | 16 unsigned int | BIT0 Low: Off BIT0 High: On | Not defined
29073 | Activate Grid Mode | 16 unsigned int | BIT0 Low: Off BIT0 High: On | Not defined
29074 | Dectivate Grid Mode | 16 unsigned int | BIT0 Low: Off BIT0 High: On | Not defined
29075 | Relay 1-6 in ECsync cabinet | 16 unsigned int | bitwise | Not defined
29076 | Eclogic PV Reference overwrite 1-8 | 16 unsigned int | bitwise | Not defined
29077 | Eclogic Bat Reference overwrite 1-8 | 16 unsigned int | bitwise | Not defined
29078 | Eclogic Bat Charge PV priority overwrite | 16 unsigned int | BIT0 Low: Grid parallel = PV Reference BIT0 High: Grid parallel = Battery BIT1 Low: Genset parallel = PV Reference BIT1 High: Genset parallel = Battery | Not defined
29079 | Eclogic P Ctrl Mode Overwrite | 16 unsigned int | BIT0: FIXED P BIT1: FIXED P PCC | Not defined
29080 | Eclogic Q Ctrl Mode Overwrite | 16 unsigned int | BIT0: FIXED Q BIT1: FIXED Q PCC BIT2: FIXED COSPHI C BIT3: FIXED COSPHI C PCC BIT4: FIXED COSPHI I BIT5: FIXED COSPHI I PCC BIT6: SHARE PF | Not defined
29081 | Eclogic Battery P Control Mode Overwrite | 16 unsigned int | BIT0: SYSTEM P BIT1: FIXED P BIT2: FIXED P SA BIT3: FIXED P PCC SA | Not defined
29082 | Eclogic Battery Q Control Mode Overwrite | 16 unsigned int | BIT0: SYSTEM Q BIT1: FIXED Q BIT2: FIXED COSPHI C BIT3: FIXED COSPHI I | Not defined
29083 | ECsync commands | 16 unsigned int | BIT0: Open ECsync breaker (Control) BIT1: Close ECsync breaker (Control) BIT2: Open ECsync breaker (Overwrite) BIT3: Close ECsync breaker (Overwrite) | Not defined
29084 | Suppress battery ctrl. functions | 16 unsigned int | BIT0: Suppress all charging BIT1: Suppress all discharging BIT2: Suppress arbitrage commands BIT3: Suppress arbitrage charge commands BIT4: Suppress arbitrage discharge commands BIT5: Suppress scheduler commands BIT6: Suppress scheduler charge commands BIT7: Suppress scheduler discharge commands BIT8: Limit P reference to DC power BIT9: Suppress ECpvX Slave BIT10: Suppress ECgrid Slave | Not defined
29085 | PV commands | 16 unsigned int | BIT0: Start PV (Control) BIT1: Stop PV (Control) BIT2: Start PV (Overwrite) BIT3: Stop PV (Overwrite) | Not defined
29086 | Battery commands | 16 unsigned int | BIT0: Start battery (Control) BIT1: Stop battery (Control) BIT2: Start battery (Overwrite) BIT3: Stop battery (Overwrite) | Not defined
29087 | Eclogic Genset PQ Mode | 16 unsigned int | BIT0 Low: Off BIT0 High: On | Not defined
29088 | Suppress PV ctrl. functions | 16 unsigned int | BIT0: Suppress SunSpec Slave | Not defined
29089 | EClogic BESS Mode | 16 unsigned int | BIT0: Selected mode for "Grid connected" BIT1: Selected mode for "Genset connected" BIT2: Selected mode for "Off" | Not defined
29090 | High priority alarms | 16 unsigned int | BIT0: Fire alarm BIT1: EPO alarm BIT2: Door open alarm | Not defined
29091..29799 | RESERVED | Not defined | Reserved for later use | Not defined
ECSync Acquisition
Address | DataLabel | DataType | Description | Not available value
29800..29815 | SN | Char, 32 byte Ascii characters | Serial number | Not defined
29816..29831 | MODEL | Char, 32 byte Ascii characters | Sync relay model | Not defined
29832 | VERSION | 16 unsigned int | Version | Not defined
29833..29899 | RESERVED | Not defined | Reserved for later use | Not defined
29900 | GRID_UL1L2 | 16 unsigned int | Line1-line2 voltage on the grid side [V] | 0xFFFF
29901 | GRID_UL2L3 | 16 unsigned int | Line2-line3 voltage on the grid side [V] | 0xFFFF
29902 | GRID_UL3L1 | 16 unsigned int | Line3-line1 voltage on the grid side [V] | 0xFFFF
29903 | GRID_UL1N | 16 unsigned int | Line1-neutral voltage on the grid side [V] | 0xFFFF
29904 | GRID_UL2N | 16 unsigned int | Line2-neutral voltage on the grid side [V] | 0xFFFF
29905 | GRID_UL3N | 16 unsigned int | Line3-neutral voltage on the grid side [V] | 0xFFFF
29906 | GRID_F1 | 16 unsigned int | L1 frequency on the grid side [0.01Hz] | 0xFFFF
29907 | GRID_F2 | 16 unsigned int | L2 frequency on the grid side [0.01Hz] | 0xFFFF
29908 | GRID_F3 | 16 unsigned int | L3 frequency on the grid side [0.01Hz] | 0xFFFF
29909 | GRID_UL1L2_ANGLE | 16 signed int | Line1-line2 voltage angle on the grid side [0.1 Deg] | 0x8000
29910 | GRID_UL2L3_ANGLE | 16 signed int | Line2-line3 voltage angle on the grid side [0.1 Deg] | 0x8000
29911 | GRID_UL3L1_ANGLE | 16 signed int | Line3-line1 voltage angle on the grid side [0.1 Deg] | 0x8000
29912 | GRID_IL1 | 16 unsigned int | line1 current [A] | 0xFFFF
29913 | GRID_IL2 | 16 unsigned int | line2 current side [A] | 0xFFFF
29914 | GRID_IL3 | 16 unsigned int | line3 current [A] | 0xFFFF
29915 | GRID_PL1 | 16 signed int | AC Power line1 [kW] | 0x8000
29916 | GRID_PL2 | 16 signed int | AC Power line2 [kW] | 0x8000
29917 | GRID_PL3 | 16 signed int | AC Power line3 [kW] | 0x8000
29918 | GRID_PTOT | 16 signed int | AC Power total [kW] | 0x8000
29919 | GRID_QL1 | 16 signed int | AC Reactive power line1 [kVAr] | 0x8000
29920 | GRID_QL2 | 16 signed int | AC Reactive power line2 [kVAr] | 0x8000
29921 | GRID_QL3 | 16 signed int | AC Reactive power line3 [kVAr] | 0x8000
29922 | GRID_QTOT | 16 signed int | AC Reactive power total [kVAr] | 0x8000
29923 | GRID_SL1 | 16 signed int | AC Apparent power line1 [kVAr] | 0x8000
29924 | GRID_SL2 | 16 signed int | AC Apparent power line2 [kVAr] | 0x8000
29925 | GRID_SL3 | 16 signed int | AC Apparent power line3 [kVAr] | 0x8000
29926 | GRID_STOT | 16 signed int | AC Apparent power total [kVAr] | 0x8000
29927 | BB_UL1L2 | 16 unsigned int | Line1-line2 voltage on the busbar side [V] | 0xFFFF
29928 | BB_UL2L3 | 16 unsigned int | Line2-line3 voltage on the busbar side [V] | 0xFFFF
29929 | BB_UL3L1 | 16 unsigned int | Line3-line1 voltage on the busbar side [V] | 0xFFFF
29930 | BB_UL1N | 16 unsigned int | Line1-neutral voltage on the busbar side [V] | 0xFFFF
29931 | BB_UL2N | 16 unsigned int | Line2-neutral voltage on the busbar side [V] | 0xFFFF
29932 | BB_UL3N | 16 unsigned int | Line3-neutral voltage on the busbar side [V] | 0xFFFF
29933 | BB_F1 | 16 unsigned int | L1 frequency on the busbar side [0.01Hz] | 0xFFFF
29934 | BB_F2 | 16 unsigned int | L2 frequency on the busbar side [0.01Hz] | 0xFFFF
29935 | BB_F3 | 16 unsigned int | L3 frequency on the busbar side [0.01Hz] | 0xFFFF
29936 | BB_UL1L2_ANGLE | 16 signed int | Line1-line2 voltage angle on the busbar side [0.1 Deg] | 0x8000
29937 | BB_UL2L3_ANGLE | 16 signed int | Line2-line3 voltage angle on the busbar side [0.1 Deg] | 0x8000
29938 | BB_UL3L1_ANGLE | 16 signed int | Line3-line1 voltage angle on the busbar side [0.1 Deg] | 0x8000
29939 | BB_GRID_UL1_ANGLE | 16 signed int | Line1-line1 voltage angle between grid and bubar side [0.1 Deg] | 0x8000
29940 | BB_GRID_UL2_ANGLE | 16 signed int | Line2-line2 voltage angle between grid and bubar side [0.1 Deg] | 0x8000
29941 | BB_GRID_UL3_ANGLE | 16 signed int | Line3-line3 voltage angle between grid and bubar side [0.1 Deg] | 0x8000
29942..29990 | RESERVED | Not defined | Reserved for later use | Not defined
29991 | STS_TRIP | 16 unsigned int | BIT5: STS Trip alarm | Not defined
29992 | BREAKER_ERROR | 16 unsigned int | BIT2: STS sync alarm BIT3: Phase seq alarm grid side BIT7: STS Open failure BIT8: STS Close failure BIT9: STS Position failure BIT11: Phase seq alarm busbar side | Not defined
29993 | MODES | 16 unsigned int | BIT3: Auto mode | Not defined
29994 | NOT_IN_AUTO | 16 unsigned int | BIT12: Not in Auto mode | Not defined
29995 | MB_SYNC_STATUS | 16 unsigned int | 0: Not synchronizing Not 0: Synchronizing | Not defined
29996 | NBR_UNACK_ALARM | 16 unsigned int | Number of unacknowleded alarms | Not defined
29997 | NBR_ALARM | 16 unsigned int | Number of alarms | Not defined
29998 | DIG_INPUTS | 16 unsigned int | Digital input status | Not defined
29999 | ALIVE | 16 unsigned int | 0: Not alive 1: Alive | Not defined
MISC AREA 1
Address | DataLabel | DataType | Description | Not available value
30000..30001 | POWER_P_DG_TOTAL | FLOAT (byte order: ABCD) | Total genset active power [kW] | Not defined
30002..30003 | POWER_Q_DG_TOTAL | FLOAT (byte order: ABCD) | Total genset reactive power [kVAr] | Not defined
30004..30005 | POWER_S_DG_TOTAL | FLOAT (byte order: ABCD) | Total genset apperant power [kVAr] | Not defined
30006..30007 | POWER_COSPHI_DG_TOTAL | FLOAT (byte order: ABCD) | Total genset cosphi | Not defined
30008 | IND_CAP_DG | 16 unsigned int | 0: Capacitive 1: Inductive | Not defined
30009..30010 | POWER_P_PV_TOTAL | FLOAT (byte order: ABCD) | Total PV active power [kW] | Not defined
30011..30012 | POWER_Q_PV_TOTAL | FLOAT (byte order: ABCD) | Total PV reactive power [kVAr] | Not defined
30013..30014 | POWER_S_PV_TOTAL | FLOAT (byte order: ABCD) | Total PV apperant power [kVAr] | Not defined
30015..30016 | POWER_COSPHI_PV_TOTAL | FLOAT (byte order: ABCD) | Total PV cosphi | Not defined
30017 | IND_CAP_PV | 16 unsigned int | 0: Capacitive 1: Inductive | Not defined
30018..30019 | POWER_P_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total Mains active power [kW] | Not defined
30020..30021 | POWER_Q_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total Mains reactive power [kVAr] | Not defined
30022..30023 | POWER_S_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total Mains apperant power [kVAr] | Not defined
30024..30025 | POWER_COSPHI_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total Mains cosphi | Not defined
30026 | IND_CAP_MAINS | 16 unsigned int | 0: Capacitive 1: Inductive | Not defined
30027..30028 | POWER_P_LOAD_TOTAL | FLOAT (byte order: ABCD) | Total active power load [kW] | Not defined
30029..30030 | POWER_Q_LOAD_TOTAL | FLOAT (byte order: ABCD) | Total reactive power load [kVAr] | Not defined
30031..30032 | POWER_S_LOAD_TOTAL | FLOAT (byte order: ABCD) | Total apperant power load [kVAr] | Not defined
30033..30034 | POWER_COSPHI_LOAD_TOTAL | FLOAT (byte order: ABCD) | Total load cosphi | Not defined
30035 | IND_CAP_LOAD | 16 unsigned int | 0: Capacitive 1: Inductive | Not defined
30036..30037 | DG_KWH_TOTAL | FLOAT (byte order: ABCD) | Total genset energy production [kWh] | Not defined
30038..30039 | DG_KWH_YEAR | FLOAT (byte order: ABCD) | Genset energy production current year [kWh] | Not defined
30040..30041 | DG_KWH_MONTH | FLOAT (byte order: ABCD) | Genset energy production current month [kWh] | Not defined
30042..30043 | DG_KWH_DAY | FLOAT (byte order: ABCD) | Genset energy production current day [kWh] | Not defined
30044..30045 | PV_KWH_TOTAL | FLOAT (byte order: ABCD) | Total PV energy production [kWh] | Not defined
30046..30047 | PV_KWH_YEAR | FLOAT (byte order: ABCD) | PV energy production current year [kWh] | Not defined
30048..30049 | PV_KWH_MONTH | FLOAT (byte order: ABCD) | PV energy production current month [kWh] | Not defined
30050..30051 | PV_KWH_DAY | FLOAT (byte order: ABCD) | PV energy production current day [kWh] | Not defined
30052..30053 | PV_KWH_CUR_TOTAL | FLOAT (byte order: ABCD) | Total PV energy production curtailed [kWh] | Not defined
30054..30055 | PV_KWH_CUR_YEAR | FLOAT (byte order: ABCD) | PV energy production curtailed current year [kWh] | Not defined
30056..30057 | PV_KWH_CUR_MONTH | FLOAT (byte order: ABCD) | PV energy production curtailed current month [kWh] | Not defined
30058..30059 | PV_KWH_CUR_DAY | FLOAT (byte order: ABCD) | PV energy production curtailed current day [kWh] | Not defined
30060..30061 | MAINS_KWH_TOTAL | FLOAT (byte order: ABCD) | Total energy imported from Mains [kWh] | Not defined
30062..30063 | MAINS_KWH_YEAR | FLOAT (byte order: ABCD) | Energy imported from Mains current year [kWh] | Not defined
30064..30065 | MAINS_KWH_MONTH | FLOAT (byte order: ABCD) | Energy imported from Mains current month [kWh] | Not defined
30066..30667 | MAINS_KWH_DAY | FLOAT (byte order: ABCD) | Energy imported from Mains current day [kWh] | Not defined
30068..30069 | MAINS_KWH_EXP_TOTAL | FLOAT (byte order: ABCD) | Total energy exported to Mains [kWh] | Not defined
30070..30071 | MAINS_KWH_EXP_YEAR | FLOAT (byte order: ABCD) | Energy exported to Mains current year [kWh] | Not defined
30072..30073 | MAINS_KWH_EXP_MONTH | FLOAT (byte order: ABCD) | Energy exported to Mains current month [kWh] | Not defined
30074..30075 | MAINS_KWH_EXP_DAY | FLOAT (byte order: ABCD) | Energy exported to Mains current day [kWh] | Not defined
30076…30077 | LOAD_KWH_TOTAL | FLOAT (byte order: ABCD) | Total energy consumed [kWh] | Not defined
30078..30079 | LOAD_KWH_YEAR | FLOAT (byte order: ABCD) | Energy consumed current year [kWh] | Not defined
30080..30081 | LOAD_KWH_MONTH | FLOAT (byte order: ABCD) | Energy consumed current month [kWh] | Not defined
30082..30083 | LOAD_KWH_DAY | FLOAT (byte order: ABCD) | Energy consumed current day [kWh] | Not defined
30084..30085 | PV_FUEL_SAVE_TOTAL | FLOAT (byte order: ABCD) | Fuel volume saving total [user defined, default: liter] | Not defined
30086..30087 | PV_FUEL_SAVE_YEAR | FLOAT (byte order: ABCD) | Fuel volume saving current year [user defined, default: liter] | Not defined
30088..30089 | PV_FUEL_SAVE_MONTH | FLOAT (byte order: ABCD) | Fuel volume saving current month [user defined, default: liter] | Not defined
30090..30091 | PV_FUEL_SAVE_DAY | FLOAT (byte order: ABCD) | Fuel volume saving current day [user defined, default: liter] | Not defined
30092..30093 | PV_FUEL_EXPEN_SAVE_TOTAL | FLOAT (byte order: ABCD) | Fuel expense savings total [user defined, default: euro] | Not defined
30094..30095 | PV_FUEL_EXPEN_SAVE_YEAR | FLOAT (byte order: ABCD) | Fuel expense savings current year [user defined, default: euro] | Not defined
30096..30097 | PV_FUEL_EXPEN_SAVE_MONTH | FLOAT (byte order: ABCD) | Fuel expense savings current month [user defined, default: euro] | Not defined
30098..30099 | PV_FUEL_EXPEN_SAVE_DAY | FLOAT (byte order: ABCD) | Fuel expense savings current day [user defined, default: euro] | Not defined
30100..30101 | PV_FUEL_EMISS_SAVE_TOTAL | FLOAT (byte order: ABCD) | CO2 emission savings total [user defined, default: kg] | Not defined
30102..30103 | PV_FUEL_EMISS_SAVE_YEAR | FLOAT (byte order: ABCD) | CO2 emission savings current year [user defined, default: kg] | Not defined
30104..30105 | PV_FUEL_EMISS_SAVE_MONTH | FLOAT (byte order: ABCD) | CO2 emission savings current month [user defined, default: kg] | Not defined
30106..30107 | PV_FUEL_EMISS_SAVE_DAY | FLOAT (byte order: ABCD) | CO2 emission savings current day [user defined, default: kg] | Not defined
30108..30109 | PV_EXP_SAVE_TOTAL | FLOAT (byte order: ABCD) | PV export yield total [user defined, default: euro] | Not defined
30110..30111 | PV_EXP_SAVE_YEAR | FLOAT (byte order: ABCD) | PV export yield current year [user defined, default: euro] | Not defined
30112..30113 | PV_EXP_SAVE_MONTH | FLOAT (byte order: ABCD) | PV export yield current month [user defined, default: euro] | Not defined
30114..30115 | PV_EXP_SAVE_DAY | FLOAT (byte order: ABCD) | PV export yield current day [user defined, default: euro] | Not defined
30116..30117 | MAINS_IMP_SAVE_TOTAL | FLOAT (byte order: ABCD) | Mains import expense savings total [user defined, default: euro] | Not defined
30118..30119 | MAINS_IMP_SAVE_YEAR | FLOAT (byte order: ABCD) | Mains import expense savings current year [user defined, default: euro] | Not defined
30120..30121 | MAINS_IMP_SAVE_MONTH | FLOAT (byte order: ABCD) | Mains import expense savings current month [user defined, default: euro] | Not defined
30122..30123 | MAINS_IMP_SAVE_DAY | FLOAT (byte order: ABCD) | Mains import expense savings current day [user defined, default: euro] | Not defined
30124..30125 | DG_FUEL_CON_TOTAL | FLOAT (byte order: ABCD) | Fuel volume consumed total [user defined, default: liter] | Not defined
30126..30127 | DG_FUEL_CON_YEAR | FLOAT (byte order: ABCD) | Fuel volume consumed current year [user defined, default: liter] | Not defined
30128..30129 | DG_FUEL_CON_MONTH | FLOAT (byte order: ABCD) | Fuel volume consumed current month [user defined, default: liter] | Not defined
30130..30131 | DG_FUEL_CON_DAY | FLOAT (byte order: ABCD) | Fuel volume consumed current day [user defined, default: liter] | Not defined
30132..30133 | DG_FUEL_EXPEN_CON_TOTAL | FLOAT (byte order: ABCD) | Fuel expense total [user defined, default: euro] | Not defined
30134..30135 | DG_FUEL_EXPEN_CON_YEAR | FLOAT (byte order: ABCD) | Fuel expense current year [user defined, default: euro] | Not defined
30136..30137 | DG_FUEL_EXPEN_CON_MONTH | FLOAT (byte order: ABCD) | Fuel expense current month [user defined, default: euro] | Not defined
30138..30139 | DG_FUEL_EXPEN_CON_DAY | FLOAT (byte order: ABCD) | Fuel expense current day [user defined, default: euro] | Not defined
30140..30141 | DG_FUEL_EMISS_CON_TOTAL | FLOAT (byte order: ABCD) | CO2 emission total [user defined, default: kg] | Not defined
30142..30143 | DG_FUEL_EMISS_CON_YEAR | FLOAT (byte order: ABCD) | CO2 emission current year [user defined, default: kg] | Not defined
30144..30145 | DG_FUEL_EMISS_CON_MONTH | FLOAT (byte order: ABCD) | CO2 emission current month [user defined, default: kg] | Not defined
30146..30147 | DG_FUEL_EMISS_CON_DAY | FLOAT (byte order: ABCD) | CO2 emission current day [user defined, default: kg] | Not defined
30148..30149 | MAINS_IMP_CON_TOTAL | FLOAT (byte order: ABCD) | Mains import expense total [user defined, default: euro] | Not defined
30150..30151 | MAINS_IMP_CON_YEAR | FLOAT (byte order: ABCD) | Mains import expense current year [user defined, default: euro] | Not defined
30152..30153 | MAINS_IMP_CON_MONTH | FLOAT (byte order: ABCD) | Mains import expense current month [user defined, default: euro] | Not defined
30154..30155 | MAINS_IMP_CON_DAY | FLOAT (byte order: ABCD) | Mains import expense current day [user defined, default: euro] | Not defined
30156..30157 | MAINS_EXP_SAVE_TOTAL | FLOAT (byte order: ABCD) | Mains export yield total [user defined, default: euro] | Not defined
30158..30159 | MAINS_EXP_SAVE_YEAR | FLOAT (byte order: ABCD) | Mains export yield current year [user defined, default: euro] | Not defined
30160..30161 | MAINS_EXP_SAVE_MONTH | FLOAT (byte order: ABCD) | Mains export yield current month [user defined, default: euro] | Not defined
30162..30163 | MAINS_EXP_SAVE_DAY | FLOAT (byte order: ABCD) | Mains export yield current day [user defined, default: euro] | Not defined
30164..30165 | PV_PENETRATION_TOTAL | FLOAT (byte order: ABCD) | PV penetration ratio total [%] | Not defined
30166..30167 | PV_PENETRATION_YEAR | FLOAT (byte order: ABCD) | PV penetration ratio current year [%] | Not defined
30168..30169 | PV_PENETRATION_MONTH | FLOAT (byte order: ABCD) | PV penetration ratio current month [%] | Not defined
30170..30171 | PV_PENETRATION_DAY | FLOAT (byte order: ABCD) | PV penetration ratio current day [%] | Not defined
30172..30173 | PV_PERFORMANCE_TOTAL | FLOAT (byte order: ABCD) | PV performance ratio total [%] | Not defined
30174..30175 | PV_PERFORMANCE_YEAR | FLOAT (byte order: ABCD) | PV performance ratio current year [%] | Not defined
30176..30177 | PV_PERFORMANCE_MONTH | FLOAT (byte order: ABCD) | PV performance ratio current month [%] | Not defined
30178..30179 | PV_PERFORMANCE_DAY | FLOAT (byte order: ABCD) | PV performance ratio current day [%] | Not defined
Genset 1 to 16 The addressses of genset number x is found by: Address_x = (x-1) * 2 + Address
30180..30181 | ACP | FLOAT (byte order: ABCD) | AC Power total [kW] | Not defined
30212..30213 | ACQ | FLOAT (byte order: ABCD) | AC Reactive power total [kVAr] | Not defined
PV 1 to 16 The addressses of PV number x is found by: Address_x = (x-1) * 2 + Address
30244..30245 | ACP | FLOAT (byte order: ABCD) | AC Power total [kW] | Not defined
30276..30277 | ACQ | FLOAT (byte order: ABCD) | AC Reactive power total [kVAr] | Not defined
Mains 1 to 16 The addressses of Mains number x is found by: Address_x = (x-1) * 2 + Address
30308..30309 | ACP | FLOAT (byte order: ABCD) | AC Power total [kW] | Not defined
30340..30341 | ACQ | FLOAT (byte order: ABCD) | AC Reactive power total [kVAr] | Not defined
Inverter 1 to 32 The addressses of inverter number x is found by: Address_x = (x-1) * 2 + Address
30372..30373 | ACP | FLOAT (byte order: ABCD) | AC Power total [kW] | Not defined
30436..30437 | ACQ | FLOAT (byte order: ABCD) | AC Reactive power total [kVAr] | Not defined
MISC AREA 2
30500..30501 | SENSOR_POA | FLOAT (byte order: ABCD) | POA irradiance [W/m2] | Not defined
30502..30503 | SENSOR_BOM | FLOAT (byte order: ABCD) | Back of module temperature [C] | Not defined
30504..30505 | PV_P_GENERATING_CAPACITY | FLOAT (byte order: ABCD) | Total PV generating capacity active power [kW] | Not defined
30506..30507 | PV_Q_GENERATING_CAPACITY | FLOAT (byte order: ABCD) | Total PV generating capacity reactive power [kVAr] | Not defined
30508..30509 | DG_P_GENERATING_CAPACITY | FLOAT (byte order: ABCD) | Total genset generating capacity active power [kW] | Not defined
30510..30511 | DG_P_LOADING_PCT | FLOAT (byte order: ABCD) | Genset active power loading [%] | Not defined
30512..30513 | DG_P_MIN_LOADING_KW | FLOAT (byte order: ABCD) | Minimum genset load [kW] | Not defined
30514..30515 | PV_P_POWER_TARGET | FLOAT (byte order: ABCD) | PV target reference active power [kW] | Not defined
30516..30517 | PV_P_POWER_REFERENCE | FLOAT (byte order: ABCD) | PV actual reference active power [kW] | Not defined
30518..30519 | PV_Q_POWER_TARGET | FLOAT (byte order: ABCD) | PV target reference reactive power [kVAr] | Not defined
30520..30521 | PV_Q_POWER_REFERENCE | FLOAT (byte order: ABCD) | PV actual reference reactive power [kVAr] | Not defined
30522..30523 | MAINS_P_GENERATING_CAPACITY | FLOAT (byte order: ABCD) | Total Mains generating capacity active power [kW] | Not defined
30524..30525 | P_PV_LOAD_PCT | FLOAT (byte order: ABCD) | PV active power loading [%] | Not defined
30526..30527 | Q_PV_LOAD_PCT | FLOAT (byte order: ABCD) | PV reactive power loading [%] | Not defined
30528..30529 | Q_DG_LOAD_PCT | FLOAT (byte order: ABCD) | Genset reactive power loading [%] | Not defined
30530..30531 | P_MAINS_LOAD_PCT | FLOAT (byte order: ABCD) | Mains active power loading [%] | Not defined
30532..30533 | Q_MAINS_LOAD_PCT | FLOAT (byte order: ABCD) | Mains reactive power loading [%] | Not defined
30534..30535 | P_PV_LOAD_ERR_PCT | FLOAT (byte order: ABCD) | PV active power error in regards to refernce [%] | Not defined
30536..30537 | Q_PV_LOAD_ERR_PCT | FLOAT (byte order: ABCD) | PV reactive power error in regards to refernce [%] | Not defined
30538..30539 | P_DG_LOAD_ERR_PCT | FLOAT (byte order: ABCD) | Genset active power error in regards to refernce [%] | Not defined
30540..30541 | Q_DG_LOAD_ERR_PCT | FLOAT (byte order: ABCD) | Genset reactive power error in regards to refernce [%] | Not defined
30542..30543 | P_MAINS_LOAD_ERR_PCT | FLOAT (byte order: ABCD) | Mains active power error in regards to refernce [%] | Not defined
30544..30545 | Q_MAINS_LOAD_ERR_PCT | FLOAT (byte order: ABCD) | Mains reactive power error in regards to refernce [%] | Not defined
30546..30547 | LATITUDE | FLOAT (byte order: ABCD) | Latitude GPS coordinate | Not defined
30548..30549 | LONGITUDE | FLOAT (byte order: ABCD) | Longitude GPS coordinate | Not defined
30550..30551 | SENSOR_GHI | FLOAT (byte order: ABCD) | GHI irradiance [W/m2] | Not defined
30552..30553 | SENSOR_AMBIENT_TEMP | FLOAT (byte order: ABCD) | Ambient temperature [C] | Not defined
30554..30555 | SENSOR_WIND_SPEED | FLOAT (byte order: ABCD) | Wind speed [m/s] | Not defined
30556..30557 | SENSOR_REL_HUMIDITY | FLOAT (byte order: ABCD) | Relative humidity [%] | Not defined
30558..30559 | SENSOR_BAR_PRES | FLOAT (byte order: ABCD) | Barometrical pressure [HPa] | Not defined
30560..30561 | SENSOR_WIND_DIR | FLOAT (byte order: ABCD) | Wind direction [deg] | Not defined
30562..30563 | SENSOR_RAIN | FLOAT (byte order: ABCD) | Rain fall [mm] | Not defined
30564..30565 | POWER_P_DG_TOTAL | FLOAT (byte order: ABCD) | Total genset active power [kW] | Not defined
30566..30567 | POWER_Q_DG_TOTAL | FLOAT (byte order: ABCD) | Total genset reactive power [kVAr] | Not defined
30568..30569 | POWER_P_PV_TOTAL | FLOAT (byte order: ABCD) | Total PV active power [kW] | Not defined
30570..30571 | POWER_Q_PV_TOTAL | FLOAT (byte order: ABCD) | Total PV reactive power [kVAr] | Not defined
30572..30573 | POWER_P_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total mains active power [kW] | Not defined
30574..30575 | POWER_Q_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total mains reactive power [kVAr] | Not defined
30576..30577 | POWER_P_LOAD_TOTAL | FLOAT (byte order: ABCD) | Total load active power [kW] | Not defined
30578..30579 | POWER_Q_LOAD_TOTAL | FLOAT (byte order: ABCD) | Total load reactive power [kVAr] | Not defined
30580..30581 | POWER_P_PV_CURTAILED | FLOAT (byte order: ABCD) | Total active power being curtailed [kW] | Not defined
30582..30583 | PV_KWH_AVA_TOTAL | FLOAT (byte order: ABCD) | Total PV energy available [kWh] | Not defined
30584..30585 | PV_KWH_AVA_YEAR | FLOAT (byte order: ABCD) | PV energy available current year [kWh] | Not defined
30586..30587 | PV_KWH_AVA_MONTH | FLOAT (byte order: ABCD) | PV energy available current month [kWh] | Not defined
30588..30589 | PV_KWH_AVA_DAY | FLOAT (byte order: ABCD) | PV energy available current day [kWh] | Not defined
30590..30591 | POWER_P_BAT_TOTAL | FLOAT (byte order: ABCD) | Total battery active power [kW] | Not defined
30592..30593 | POWER_Q_BAT_TOTAL | FLOAT (byte order: ABCD) | Total battery reactive power [kVAr] | Not defined
30594..30595 | POWER_S_BAT_TOTAL | FLOAT (byte order: ABCD) | Total battery apparent power [kVA] | Not defined
30596..30597 | COSPHI_BAT_TOTAL | FLOAT (byte order: ABCD) | Cosphi Battery [%] | Not defined
30598 | COSPHI_BAT_IND_CAP | 16 unsigned int | Cosphi capacitive | Not defined
30599..30600 | BATTERY_P_GENERATING_CAPACITY | FLOAT (byte order: ABCD) | Total Battery inverter generating capacity active power [kW] | Not defined
30601..30602 | BATTERY_Q_GENERATING_CAPACITY | FLOAT (byte order: ABCD) | Total Battery inverter generating capacity reactive power [kVAr] | Not defined
30603..30604 | BATTERY_P_POWER_TARGET | FLOAT (byte order: ABCD) | Active Power Battery Reference [kW] | Not defined
30605..30606 | BATTERY_P_POWER_REFERENCE | FLOAT (byte order: ABCD) | Active Power Battery Reference Ramped [kW] | Not defined
30607..30608 | BATTERY_Q_POWER_TARGET | FLOAT (byte order: ABCD) | Reactive Power Battery Reference [kW] | Not defined
30609..30610 | BATTERY_Q_POWER_REFERENCE | FLOAT (byte order: ABCD) | Reactive Power Battery Reference Ramped [kW] | Not defined
30611..30612 | P_BATTERY_LOAD_PCT | FLOAT (byte order: ABCD) | Battery active power loading [%] | Not defined
30613..30614 | Q_BATTERY_LOAD_PCT | FLOAT (byte order: ABCD) | Battery reactive power loading [%] | Not defined
30615..30616 | P_BATTERY_LOAD_ERR_PCT | FLOAT (byte order: ABCD) | Battery active power error in regards to refernce [%] | Not defined
30617..30618 | Q_BATTERY_LOAD_ERR_PCT | FLOAT (byte order: ABCD) | Battery reactive power error in regards to refernce [%] | Not defined
30619..30620 | BATTERY_SOC_PCT | FLOAT (byte order: ABCD) | Battery State Of Charge [%] | Not defined
30621..30622 | BATTERY_SOH_PCT | FLOAT (byte order: ABCD) | Battery State Of Health [%] | Not defined
30623..30624 | BATTERY_SOE_KWH | FLOAT (byte order: ABCD) | Battery State Of Energy [kWh] | Not defined
30625..30626 | BATTERY_ODC_KW | FLOAT (byte order: ABCD) | Battery online discharge capacity [kW] | Not defined
30627..30628 | BATTERY_OCC_KW | FLOAT (byte order: ABCD) | Battery online charge capacity [kW] | Not defined
30629..30630 | BATTERY_EFC_TOTAL | FLOAT (byte order: ABCD) | EFC counter total | Not defined
30631..30632 | BATTERY_EFC_YEAR | FLOAT (byte order: ABCD) | EFC counter year | Not defined
30633..30634 | BATTERY_EFC_MONTH | FLOAT (byte order: ABCD) | EFC counter month | Not defined
30635..30636 | BATTERY_EFC_DAY | FLOAT (byte order: ABCD) | EFC counter day | Not defined
30637..30638 | BATTERY_DOD_TOTAL | FLOAT (byte order: ABCD) | DOD counter total | Not defined
30639..30640 | BATTERY_DOD_YEAR | FLOAT (byte order: ABCD) | DOD counter year | Not defined
30641..30642 | BATTERY_DOD_MONTH | FLOAT (byte order: ABCD) | DOD counter month | Not defined
30643..30644 | BATTERY_DOD_DAY | FLOAT (byte order: ABCD) | DOD counter day | Not defined
30645..30646 | FUEL_LEVEL_01 | FLOAT (byte order: ABCD) | Fuel level 01 [%] | Not defined
30647..30648 | FUEL_LEVEL_02 | FLOAT (byte order: ABCD) | Fuel level 02 [%] | Not defined
30649..30650 | FUEL_LEVEL_03 | FLOAT (byte order: ABCD) | Fuel level 03 [%] | Not defined
30651..30652 | FUEL_LEVEL_04 | FLOAT (byte order: ABCD) | Fuel level 04 [%] | Not defined
30653..30654 | FUEL_PRESS_01 | FLOAT (byte order: ABCD) | Fuel press 01 [bar] | Not defined
30655..30656 | FUEL_PRESS_02 | FLOAT (byte order: ABCD) | Fuel press 01 [bar] | Not defined
30657..30658 | FUEL_PRESS_03 | FLOAT (byte order: ABCD) | Fuel press 01 [bar] | Not defined
30659..30660 | FUEL_PRESS_04 | FLOAT (byte order: ABCD) | Fuel press 01 [bar] | Not defined
30661 | MIN_CELL_VOLTAGE | 16 unsigned int | Minimum cell voltage [mV] | Not defined
30662 | MAX_CELL_VOLTAGE | 16 unsigned int | Maximum cell voltage [mV] | Not defined
30663 | MIN_CELL_TEMPERATURE | 16 signed int | Minimum cell temperature [0.1C] | Not defined
30664 | MAX_CELL_TEMPERATURE | 16 signed int | Maximum cell temperature [0.1C] | Not defined
30665 | BMS_STATE | 16 unsigned int | BMS state | Not defined
30666..30667 | POWER_P_DCPV_TOTAL | FLOAT (byte order: ABCD) | Total PV active power [kW] | Not defined
30668..30699 | Reserved | Not defined | Reserved for later use | Not defined
30700..30701 | P_BATTERY_INV_POWER | FLOAT (byte order: ABCD) | Active power from battery inverter [kW] | Not defined
30702..30763 | Reserved | Not defined | Reserved for later use | Not defined
30764..30765 | Q_BATTERY_INV_POWER | FLOAT (byte order: ABCD) | Reactive power from battery inverter [kW] | Not defined
30766..30827 | Reserved | not defined | Reserved for later use | Not defined
30828..30829 | PV_P_POWER_REFERENCE_PCT | FLOAT (byte order: ABCD) | PV actual reference active power [%] | Not defined
30830..30831 | PV_Q_POWER_REFERENCE_PCT | FLOAT (byte order: ABCD) | PV actual reference reactive power [%] | Not defined
30832..30833 | BAT_P_POWER_REFERENCE_PCT | FLOAT (byte order: ABCD) | Active Power Battery Reference Ramped [%] | Not defined
30834..30835 | BAT_Q_POWER_REFERENCE_PCT | FLOAT (byte order: ABCD) | Reactive Power Battery Reference Ramped [%] | Not defined
30836..30899 | Reserved | Not defined | Reserved for later use | Not defined
30900..30901 | BATTERY_ENERGY_TOTAL | FLOAT (byte order: ABCD) | Battery energy total [kWh] | Not defined
30902..30903 | BATTERY_ENERGY_YEAR | FLOAT (byte order: ABCD) | Battery energy year [kWh] | Not defined
30904..30305 | BATTERY_ENERGY_MONTH | FLOAT (byte order: ABCD) | Battery energy month [kWh] | Not defined
30906..30907 | BATTERY_ENERGY_DAY | FLOAT (byte order: ABCD) | Battery energy day [kWh] | Not defined
30908..30909 | BATTERY_IMP_TOTAL | FLOAT (byte order: ABCD) | Battery imported total [kWh] | Not defined
30910..30911 | BATTERY_IMP_YEAR | FLOAT (byte order: ABCD) | Battery imported year [kWh] | Not defined
30912..30913 | BATTERY_IMP_MONTH | FLOAT (byte order: ABCD) | Battery imported month [kWh] | Not defined
30914..30915 | BATTERY_IMP_DAY | FLOAT (byte order: ABCD) | Battery imported day [kWh] | Not defined
30916..30917 | BATTERY_ENERGY_PV_IN_TOTAL | FLOAT (byte order: ABCD) | PV energy fed into the battery total [kWh] | Not defined
30918..30919 | BATTERY_ENERGY_PV_IN_YEAR | FLOAT (byte order: ABCD) | PV energy fed into the battery year [kWh] | Not defined
30920..30321 | BATTERY_ENERGY_PV_IN_MONTH | FLOAT (byte order: ABCD) | PV energy fed into the battery month [kWh] | Not defined
30922..30923 | BATTERY_ENERGY_PV_IN_DAY | FLOAT (byte order: ABCD) | PV energy fed into the battery day [kWh] | Not defined
30924..30925 | BATTERY_ENERGY_PV_OUT_TOTAL | FLOAT (byte order: ABCD) | PV energy discharged from the battery total [kWh] | Not defined
30926..30927 | BATTERY_ENERGY_PV_OUT_YEAR | FLOAT (byte order: ABCD) | PV energy discharged from the battery year [kWh] | Not defined
30928..30329 | BATTERY_ENERGY_PV_OUT_MONTH | FLOAT (byte order: ABCD) | PV energy discharged from the battery month [kWh] | Not defined
30930..30931 | BATTERY_ENERGY_PV_OUT_DAY | FLOAT (byte order: ABCD) | PV energy discharged from the battery day [kWh] | Not defined
30932..30933 | BATTERY_ENERGY_PV_AVAIL | FLOAT (byte order: ABCD) | PV energy available in the battery [kWh] | Not defined
30934..30935 | BATTERY_ENERGY_DG_IN_TOTAL | FLOAT (byte order: ABCD) | Genset energy fed into the battery total [kWh] | Not defined
30936..30937 | BATTERY_ENERGY_DG_IN_YEAR | FLOAT (byte order: ABCD) | Genset energy fed into the battery year [kWh] | Not defined
30938..30339 | BATTERY_ENERGY_DG_IN_MONTH | FLOAT (byte order: ABCD) | Genset energy fed into the battery month [kWh] | Not defined
30940..30941 | BATTERY_ENERGY_DG_IN_DAY | FLOAT (byte order: ABCD) | Genset energy fed into the battery day [kWh] | Not defined
30942..30943 | BATTERY_ENERGY_DG_OUT_TOTAL | FLOAT (byte order: ABCD) | Genset energy discharged from the battery total [kWh] | Not defined
30944..30945 | BATTERY_ENERGY_DG_OUT_YEAR | FLOAT (byte order: ABCD) | Genset energy discharged from the battery year [kWh] | Not defined
30946..30347 | BATTERY_ENERGY_DG_OUT_MONTH | FLOAT (byte order: ABCD) | Genset energy discharged from the battery month [kWh] | Not defined
30948..30949 | BATTERY_ENERGY_DG_OUT_DAY | FLOAT (byte order: ABCD) | Genset energy discharged from the battery day [kWh] | Not defined
30950..30951 | BATTERY_ENERGY_DG_AVAIL | FLOAT (byte order: ABCD) | Genset energy available in the battery [kWh] | Not defined
30952..30953 | BATTERY_ENERGY_MAINS_IN_TOTAL | FLOAT (byte order: ABCD) | Mains energy fed into the battery total [kWh] | Not defined
30954..30955 | BATTERY_ENERGY_MAINS_IN_YEAR | FLOAT (byte order: ABCD) | Mains energy fed into the battery year [kWh] | Not defined
30956..30357 | BATTERY_ENERGY_MAINS_IN_MONTH | FLOAT (byte order: ABCD) | Mains energy fed into the battery month [kWh] | Not defined
30958..30959 | BATTERY_ENERGY_MAINS_IN_DAY | FLOAT (byte order: ABCD) | Mains energy fed into the battery day [kWh] | Not defined
30960..30961 | BATTERY_ENERGY_MAINS_OUT_TOTAL | FLOAT (byte order: ABCD) | Mains energy discharged from the battery total [kWh] | Not defined
30962..30963 | BATTERY_ENERGY_MAINS_OUT_YEAR | FLOAT (byte order: ABCD) | Mains energy discharged from the battery year [kWh] | Not defined
30964..30365 | BATTERY_ENERGY_MAINS_OUT_MONTH | FLOAT (byte order: ABCD) | Mains energy discharged from the battery month [kWh] | Not defined
30966..30967 | BATTERY_ENERGY_MAINS_OUT_DAY | FLOAT (byte order: ABCD) | Mains energy discharged from the battery day [kWh] | Not defined
30968..30969 | BATTERY_ENERGY_MAINS_AVAIL | FLOAT (byte order: ABCD) | Mains energy available in the battery [kWh] | Not defined
30970..30998 | Reserved
30999 | ECPV_SW_VERSION | 16 unsigned int | SW version opf the Ecpv application SW
BITFIELD AREA 1
31000 | BITFIELD_1 | 16 unsigned int | GB ON 1..16 | Not defined
31001 | BITFIELD_2 | 16 unsigned int | MB ON 1..16 | Not defined
31002 | BITFIELD_3 | 16 unsigned int | BIT0: Any GB ON BIT1: Any MB ON BIT2: Curtailment active BIT3: PV started BIT4: PV stopped BIT5: Genset management: Genset mode active BIT6: Genset management: Genset mode inactive BIT7: Simulation: Active BIT8: Night time: Active BIT9: Show ECpanel password in clear text BIT10: Battery Started BIT11: Battery stopped BIT12: Grid management: Grid mode active BIT13: Grid management: Grid mode inactive BIT14: STS Open | Not defined
31003 | BITFIELD_4 | 16 unsigned int | BIT0: Any inverter missing BIT1: Inverter socket connection alarm BIT2: Any genset meter missing BIT3: Genset meter socket connection alarm BIT4: Any PV meter missing BIT5: PV meter socket connection alarm BIT6: Any Mains meter missing BIT7: Mains meter socket connection alarm BIT8: Sensor 1 missing BIT9: Sensor 2 missing BIT10: Sensor 3 missing BIT11: Sensor 4 missing BIT12: SunSpec incompatible BIT13: COM2 slave timeout BIT14: COM3 slave timeout BIT15: TCP slave timeout | Not defined
31004 | BITFIELD_5 | 16 unsigned int | BIT0: Event log FTP fail BIT1: Production log FTP fail BIT2: Summary log FTP fail BIT3: Test FTP fail BIT4: Event log mail fail BIT5: Production log mail fail BIT6: Summary log mail fail BIT7: Test mail fail BIT8: Bat meter missing BIT9: Bat meter socket connection alarm | Not defined
31005 | BITFIELD_6 | 16 unsigned int | BIT0: Genset low power alarm BIT1: Mains low power alarm BIT2: DG management: Genset start failure alarm BIT3: DG management: Genset stop failure alarm BIT4: Comm 2 slave timeout alarm BIT5: Comm 3 slave timeout alarm BIT6: TCP slave timeout alarm BIT7: SOC maximum alarm BIT8: SOC minimum alarm BIT9: Fuel level alarm BIT10: Common comm alarm BIT11: Inverter deviation alarm BIT12: Cell voltage maximum alarm BIT13: Cell voltage minimum alarm | Not defined
31006 | BITFIELD_7 | 16 unsigned int | Inverter 01-16 missing | Not defined
31007 | BITFIELD_8 | 16 unsigned int | Inverter 17-32 missing | Not defined
31008 | BITFIELD_9 | 16 unsigned int | DG meter 01-16 missing | Not defined
31009 | BITFIELD_10 | 16 unsigned int | PV meter 01-16 missing | Not defined
31010 | BITFIELD_11 | 16 unsigned int | Mains meter 01-16 missing | Not defined
31011 | BITFIELD_12 | 16 unsigned int | DG Management start commands 01..16 | Not defined
31012 | BITFIELD_13 | 16 unsigned int | DG power detected 01..16 | Not defined
31013 | BITFIELD_14 | 16 unsigned int | BIT0: IO module 1 missing BIT1: IO module 2 missing BIT2: IO module 3 missing BIT3: IO module 4 missing | Not defined
31014 | BITFIELD_15 | 16 unsigned int | EClogic Threshold output 01..16 | Not defined
31015 | BITFIELD_16 | 16 unsigned int | Battery inverter 01..16 missing | Not defined
31016 | BITFIELD_17 | 16 unsigned int | BIT0: Any Battery inverter missing BIT1: Battery inverter socket connection alarm BIT2: Any BMS missing BIT3: BMS socket connection alarm BIT4: Any HVAC missing BIT5: HVAC socket connection alarm BIT6: Any ECsync missing BIT7: ECsync socket connection alarm BIT8: Any ECpvX slave blocked BIT9: Any ECpvX slave missing BIT10: Any ECpvX slave Bat inverter missing BIT11: All ECpvX slave Bat inverter missing | Not defined
31017 | BITFIELD_18 | 16 unsigned int | Grid management MB pos on | Not defined
31018 | BITFIELD_19 | 16 unsigned int | BIT0: Command timer 01 active BIT1: Command timer 02 active BIT2: Command timer 03 active BIT3: Command timer 04 active BIT4: DG charge timer active BIT5: Mains charge timer active BIT6: Mains charge scheduler, charge enabled BIT7: Dispatch power when DG connected disabled BIT8: Dispatch power when grid is connected disabled BIT9: Mains charge scheduler, discharge enabled BIT10: Mains spotprice optimizer, charge enabled BIT11: Mains spotprice optimizer, discharge enabled BIT12: Grid Connect Okay BIT13: Grid Disonnect Okay BIT14: Grid Connect Okay Timer BIT15: Grid Disonnect Okay Timer | Not defined
31019 | BITFIELD_20 | 16 unsigned int | Command Panel buttons 01..16 | Not defined
31020 | BITFIELD_21 | 16 unsigned int | BIT0: Battery ready BIT1: Battery running BIT2: Battery deloaded | Not defined
31021 | BITFIELD_22 | 16 unsigned int | EClogic Timers elapsed 01..16 | Not defined
31022 | BITFIELD_23 | 16 unsigned int | EClogic Modbus Event 01..16 | Not defined
31023 | BITFIELD_24 | 16 unsigned int | EClogic Modbus Event 17..32 | Not defined
31024 | BITFIELD_25 | 16 unsigned int | BIT0: EClogic alarm 01 active BIT1:EClogic alarm 02 active BIT2: EClogic alarm 03 active BIT3: EClogic alarm 04 active BIT4: EClogic alarm 05 active BIT5:EClogic alarm 06 active BIT6: EClogic alarm 07 active BIT7: EClogic alarm 08 active | Not defined
31025 | BITFIELD_26 | 16 unsigned int | BIT0: HVAC internal fan ON BIT1: HVAC external fan ON BIT2: HVAC heating ON BIT3: HVAC cooling ON BIT4: HVAC Sensor fault BIT5: HVAC High voltage alarm BIT6: HVAC temperature alarm BIT7: HVAC pressure alarm BIT8: HVAC compressor fault BIT9: HVAC heater fault BIT10: HVAC internal fan alarm BIT11: HVAC external fan alarm | Not defined
31026 | BITFIELD_27 | 16 unsigned int | Battery meter 01-16 missing | Not defined
31027 | BITFIELD_28 | 16 unsigned int | BIT0: ECsync STS synchronizing failure BIT1: ECsync STS Open failure BIT2: ECsync Close failure BIT3: ECsync Position failure BIT4: ECsync Phase sequence alarm BIT5: ECsync STS Trip alarm BIT6: ECsync Any unack. alarm BIT7: ECsync Any alarms BIT8: ECsync Not in auto mode alarm BIT9: Emg. Stop | Not defined
31028 | BITFIELD_29 | 16 unsigned int | BIT0: Meas/Ctrl CB Feedbacks BIT1: ECsync External Mains breaker closed BIT2: ECsync External Genset breaker closed BIT3: ECsync STS Open BIT4: ECsync STS Synchronizing BIT5: ECsync STS Open command active BIT6: ECsync STS Close command active | Not defined
31029 | BITFIELD_30 | 16 unsigned int | ECapi Command 01..16 | Not defined
31030 | BITFIELD_31 | 16 unsigned int | ECapi Command 17..32 | Not defined
SETTINGS AREA
31700 | NBR_INVERTERS | 16 unsigned int | Number of inverters | Not defined
31701 | NBR_DG_METERS | 16 unsigned int | Number of genset meters | Not defined
31702 | NBR_PV_METERS | 16 unsigned int | Number of PV meters | Not defined
31703 | NBR_MAINS_METERS | 16 unsigned int | Number of mains meters | Not defined
31704 | SENSORS_ENABLED | 16 unsigned int | Bitwise 0: POA 1: BOM 2: GHI 3: Ambient temp. 4: Wind speed 5: Relative humidity 6: Bar pressure 7: Wind direction 8: Rain 9: Fuel level 01 10: Fuel level 02 11: Fuel level 03 12: Fuel level 04 14: Mains present 15: Genset present | Not defined
31705/31706 | INSTALLED_P_CAPACITY | FLOAT (byte order: ABCD) | installed panel capacity in kW | Not defined
31707 | INVERTER_PROTOCOL_SELECTED | 16 unsigned int | Inverter protocol selected | Not defined
31708 | DG_METER_PROTOCOL_SELECTED | 16 unsigned int | Genset meter protocol selected | Not defined
31709 | PV_METER_PROTOCOL_SELECTED | 16 unsigned int | PV meter protocol selected | Not defined
31710 | MAINS_METER_PROTOCOL_SELECTED | 16 unsigned int | Mains meter protocol selected | Not defined
31711..31715 | CURRENCY | string | Currency | Not defined
31716..31720 | VOLUME | string | Volume | Not defined
31721..31725 | MASS | string | Mass | Not defined
31726 | PV_CONTROL | Enum | PV control enabled 0: DISABLED 1: ENABLED | Not defined
31727 | GENSET_MANAGEMENT | Enum | Genset management enabled 0: DISABLED 1: ENABLED | Not defined
31728 | SUNSPEC_SLAVE | Enum | SunSpec slave enabled 0: DISABLED 1: ENABLED | Not defined
31729 | PROPRIERATY_SLAVE | Enum | Proprietary slave enabled 0: DISABLED 1: ENABLED | Not defined
31730 | IOS_ENABLED | 16 unsigned int | Bitwise 0: IO module 1 1: IO module 2 2: IO module 3 3: IO module 4 | Not defined
31731/31732 | INSTALLED_S_CAPACITY | FLOAT (byte order: ABCD) | installed inverter capacity in kVA | Not defined
31733/31734 | INSTALLED_Q_CAPACITY | FLOAT (byte order: ABCD) | installed inverter capacity in kVAr | Not defined
31735 | BAT_INVERTER_PROTOCOL_SELECTED | 16 unsigned int | Battery inverter protocol selected | Not defined
31736 | BAT_CONTROL | Enum | Battery control enabled 0: DISABLED 1: ENABLED | Not defined
31737 | NBR_BAT_INVERTERS | 16 unsigned int | Number of battery inverters | Not defined
31738 | GRID_MANAGEMENT | Enum | Grid management enabled 0: DISABLED 1: ENABLED | Not defined
31739/31740 | INSTALLED_S_BATCAPACITY | FLOAT (byte order: ABCD) | installed battery inverter capacity in kVA | Not defined
31741/31742 | INSTALLED_Q_BATCAPACITY | FLOAT (byte order: ABCD) | installed battery inverter capacity in kVAr | Not defined
31743/31744 | INSTALLED_P_BATCAPACITY | FLOAT (byte order: ABCD) | installed battery capacity in kW | Not defined
31745/31746 | INSTALLED_H_BATCAPACITY | FLOAT (byte order: ABCD) | installed battery capacity in hours | Not defined
31747 | PV_CONTROL_SEC | Enum | PV control secondary enabled 0: DISABLED 1: ENABLED | Not defined
31748 | NUMBER_LGR_DG_METERS | 16 unsigned int | Number of Load meters in DG range. | Not defined
31749 | NUMBER_LGR_PV_METERS | 16 unsigned int | Number of Load meters in PV range. | Not defined
31750 | NUMBER_LGR_MAINS_METERS | 16 unsigned int | Number of Load meters in Mains range. | Not defined
31751 | SENSORS_02_ENABLED | 16 unsigned int | Bitwise 0: Fuel pressure 01 1: Fuel pressure 02 2: Fuel pressure 03 3: Fuel pressure 04 | Not defined
31752 | BMS_PROTOCOL_SELECTED | 16 unsigned int | BMS protocol selected | Not defined
31753 | HVAC_PROTOCOL_SELECTED | 16 unsigned int | HVAC protocol selected | Not defined
31754 | NBR_BAT_METERS | 16 unsigned int | Number of battery meters | Not defined
31755 | BAT_METER_PROTOCOL_SELECTED | 16 unsigned int | Battery meter protocol selected | Not defined
31756 | ECSYNC_PROTOCOL_SELECTED | 16 unsigned int | ECsync protocol selected | Not defined
31757 | ECGRID_SLAVE | Enum | ECgrid slave enabled 0: DISABLED 1: ENABLED | Not defined
RTC CLOCK
32000 | Year | 16 unsigned int | ECpv RTC year | Not defined
32001 | Month | 16 unsigned int | ECpv RTC month | Not defined
32002 | Date | 16 unsigned int | ECpv RTC date | Not defined
32003 | Hour | 16 unsigned int | ECpv RTC hour | Not defined
32004 | Minute | 16 unsigned int | ECpv RTC minute | Not defined
32005 | Second | 16 unsigned int | ECpv RTC second | Not defined
32006 | Millisecond | 16 unsigned int | ECpv RTC millisecond | Not defined
IO MODULE INFO
32010 | IO_TYPE_01 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32011 | IO_TYPE_02 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32012 | IO_TYPE_03 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32013 | IO_TYPE_04 | 16 unsigned int | 0: OFF 1: EX0008DD 2: EX1600DD 3: EX1608DD 4: SX08R 5: ECPVX 6: Huawei smartlogger 7: EX04AIO 8: EX04AIS 9: DEIF BTB 10: DSE8610 11: Woodward LS-5
32014 | IO_ANALOGUE_TYPE_SELECTED | 16 unsigned int | BIT0: Module 1 is analogue type BIT1: Module 2 is analogue type BIT2: Module 3 is analogue type BIT3: Module 4 is analogue type
32020..32039 | INFOTEXT_MODULE_01 | string | Info text for Module 1 type | Not defined
32040..32059 | INFOTEXT_MODULE_02 | string | Info text for Module 2 type | Not defined
32060..32079 | INFOTEXT_MODULE_03 | string | Info text for Module 3 type | Not defined
32080..32099 | INFOTEXT_MODULE_04 | string | Info text for Module 4 type | Not defined
INFO&MODE TEXT
32100..32119 | INFOTEXT_GENSET | string | Info text for Genset | Not defined
32120..32139 | INFOTEXT_PV | string | Info text for PV | Not defined
32140..32159 | INFOTEXT_GRID | string | Info text for Grid | Not defined
32160..32179 | INFOTEXT_BATTERY | string | Info text for Battery | Not defined
32180..32199 | MODETEXT_GENSET | string | Mode text for Genset | Not defined
32200..32219 | MODETEXT_GRID | string | Mode text for Grid | Not defined
32220..32239 | MODETEXT_BATTERY | string | Mode text for Battery | Not defined
32300 | TOTAL_DG_LOAD_METERS | 16 unsigned int | Total number of DG and load meters | Not defined
32301 | TOTAL_PV_LOAD_METERS | 16 unsigned int | Total number of PV and load meters | Not defined
32302 | TOTAL_MAINS_LOAD_METERS | 16 unsigned int | Total number of Mains and load meters | Not defined
32303 | NBR_TOT_INV_SEC_INV | 16 unsigned int | LowByte: Total number of inverters highByte: Number of secondary inverters | Not defined
32304 | INV_PROT_PRIM_SEC | 16 unsigned int | LowByte: Primary inverter protocol highByte: Secondary inverter protocol | Not defined
STAUS TEXTS
32400..32479 | STATUS_TEXT_01 | string | Status text in line 1 | Not defined
32480..32559 | STATUS_TEXT_02 | string | Status text in line 2 | Not defined
32560..32639 | STATUS_TEXT_03 | string | Status text in line 3 | Not defined
32640 | STATUS_TEXT_01_ACK_POSSIBLE | enum16 | 0: NOT POSSIBLE 1: POSSIBLE | Not defined
32641 | STATUS_TEXT_02_ACK_POSSIBLE | enum16 | 0: NOT POSSIBLE 1: POSSIBLE | Not defined
32642 | STATUS_TEXT_03_ACK_POSSIBLE | enum16 | 0: NOT POSSIBLE 1: POSSIBLE | Not defined
32643 | NBR_OF_STATUS_TEXTS | 16 unsigned int | Number of status texts displayed | Not defined
32644 | MIN_SLIDER | 16 signed int | Minimum possible status text slider value | Not defined

## Holding Register 0x03
Proprietary profile
Address | DataLabel | DataType | Description | Note
Page01 (Settings) |  |  |  | Page01 need to be enabled
0 | Reserved
1 | Mains P control mode | enum16 | 0: FIXED P 1: FIXED P PCC
2..3 | Mains P reference | FLOAT (byteorder: ABCD) | Active power reference in kW when parallel to grid
4 | Mains Q control mode | enum16 | 0: FIXED Q 1: FIXED Q PCC 2: FIXED COSPHI C 3: FIXED COSPHI C PCC 4: FIXED COSPHI I 5: FIXED COSPHI I PCC
5..6 | Mains Q reference | FLOAT (byteorder: ABCD) | Reactive power reference in kVAr when parallel to grid and a Q ctrl method selected
7..8 | Mains cosphi reference | FLOAT (byteorder: ABCD) | Cosphi reference when parallel to grid and a cosphi ctrl method selected
9..10 | Minimum genset load | FLOAT (byteorder: ABCD) | Minimum genset operating load in percentage
11 | Genset Q control mode | enum16 | 0: ALL Q 1: SHARING Q 2: SAME COSPHI 3: FIXED COSPHI C DG 4: FIXED COSPHI I DG
12..13 | DG cosphi cap reference | FLOAT (byteorder: ABCD) | Cap cosphi reference when parallel to genset and "FIXED COSPHI C DG" selected
14..15 | DG cosphi ind reference | FLOAT (byteorder: ABCD) | Ind cosphi reference when parallel to genset and "FIXED COSPHI I DG" selected
16..17 | PV P Ramp up | FLOAT (byteorder: ABCD) | PV power ramp up rate [%/s]
18..19 | PV P Ramp down | FLOAT (byteorder: ABCD) | PV power ramp down rate [%/s]
20..21 | PV Q Ramp up | FLOAT (byteorder: ABCD) | PV reactive power ramp up rate [%/s]
22..23 | PV Q Ramp down | FLOAT (byteorder: ABCD) | PV reactive power ramp down rate [%/s]
24..25 | PV Mains Parallel P Ramp up | FLOAT (byteorder: ABCD) | PV power ramp up rate [%/s] when parallel to grid
26..27 | PV Mains Parallel P Ramp down | FLOAT (byteorder: ABCD) | PV power ramp down rate [%/s] when parallel to grid
28..29 | PV Mains Parallel Q Ramp up | FLOAT (byteorder: ABCD) | PV reactive power ramp up rate [%/s] when parallel to grid
30..31 | PV Mains Parallel Q Ramp down | FLOAT (byteorder: ABCD) | PV reactive power ramp down rate [%/s] when parallel to grid
32..63 | DG 01..16 Rated power | FLOAT (byteorder: ABCD) | Rated power of genset 01..16
64..65 | Battery P Ramp up | FLOAT (byteorder: ABCD) | Battery power ramp up rate [%/s]
66..67 | Battery P Ramp down | FLOAT (byteorder: ABCD) | Battery power ramp down rate [%/s]
68..69 | Battery Q Ramp up | FLOAT (byteorder: ABCD) | Battery reactive power ramp up rate [%/s]
70..71 | Battery Q Ramp down | FLOAT (byteorder: ABCD) | Battery reactive power ramp down rate [%/s]
72..73 | Battery Mains Parallel P Ramp up | FLOAT (byteorder: ABCD) | Battery power ramp up rate [%/s] when parallel to grid
74..75 | Battery Mains Parallel P Ramp down | FLOAT (byteorder: ABCD) | Battery power ramp down rate [%/s] when parallel to grid
76..77 | Battery Mains Parallel Q Ramp up | FLOAT (byteorder: ABCD) | Battery reactive power ramp up rate [%/s] when parallel to grid
78..79 | Battery Mains Parallel Q Ramp down | FLOAT (byteorder: ABCD) | Battery reactive power ramp down rate [%/s] when parallel to grid
80 | Battery Charge PV Enable | enum16 | 0: DISABLE 1: ENABLE
81 | Battery Charge Mains Enable | enum16 | 0: DISABLE 1: ENABLE 2: TIMER
82 | Battery Charge DG Enable | enum16 | 0: DISABLE 1: ENABLE 2: TIMER
83..84 | Battery Charge PV Start SOC | FLOAT (byteorder: ABCD) | Battery SOC start set point for PV charging [%]
85..86 | Battery Charge PV Stop SOC | FLOAT (byteorder: ABCD) | Battery SOC stop set point for PV charging [%]
87..88 | Battery Charge DG Start SOC | FLOAT (byteorder: ABCD) | Battery SOC start set point for DG charging [%]
89..90 | Battery Charge DG Stop SOC | FLOAT (byteorder: ABCD) | Battery SOC stop set point for DG charging [%]
91..92 | Battery Charge DG max load pct | FLOAT (byteorder: ABCD) | Maximum load percentage on gensets when charging the battery [%]
93..94 | Battery Charge Mains Start SOC | FLOAT (byteorder: ABCD) | Battery SOC start set point for Mains charging [%]
95..96 | Battery Charge Mains Stop SOC | FLOAT (byteorder: ABCD) | Battery SOC stop set point for Mains charging [%]
97..98 | Battery Charge Mains max load pct | FLOAT (byteorder: ABCD) | Maximum load percentage on Mains when charging the battery [%]
99 | Mains Battery P control mode | enum16 | 0: SYSTEM P 1: FIXED P
100..101 | Mains Battery P reference | FLOAT (byteorder: ABCD) | Active power reference in kW when parallel to grid
102 | Mains Battery Q control mode | enum16 | 0: SYSTEM Q 1: FIXED Q 2: FIXED COSPHI C 3: FIXED COSPHI I
103..104 | Mains Battery Q reference | FLOAT (byteorder: ABCD) | Reactive power reference in kVAr when parallel to grid and a Q ctrl method selected
105..106 | Mains Battery cosphi reference | FLOAT (byteorder: ABCD) | Cosphi reference when parallel to grid and a cosphi ctrl method selected
107 | Backup In Off Mode Enable | enum16 | The genset will act as backup for for the battery in off mode
108..109 | Connect threshold genset | FLOAT (byteorder: ABCD) | Connect threshold for backup in off mode with genset [%]
110..111 | Disconnect threshold genset | FLOAT (byteorder: ABCD) | Disconnect threshold for backup in off mode with genset [%]
112 | Generator breaker sync Enable | enum16 | Synchronizing generator breaker
113..114 | Generator breaker open point | FLOAT (byteorder: ABCD) | Open point for stop signal to the generator [%]
115 | Grid backup Enable | enum16 | Genset backup if grid fails
116 | Genset management enable | enum16 | Genset management enable.
117 | Backup In Off Mode Enable | enum16 | The grid will act as backup for for the battery in off mode
118..119 | Connect threshold genset | FLOAT (byteorder: ABCD) | Connect threshold for backup in off mode with grid [%]
120..121 | Disconnect threshold genset | FLOAT (byteorder: ABCD) | Disconnect threshold for backup in off mode with grid [%]
122 | Grid breaker sync Enable | enum16 | Synchronizing grid breaker
123..124 | Grid breaker open point | FLOAT (byteorder: ABCD) | Open point for open signal to the grid breaker [%]
125 | Genset backup Enable | enum16 | Grid backup if genset fails
126 | Grid management enable | enum16 | Grid management enable.
127 | Battery grid support enable | enum16 | Battery will support the grid in case of failure.
128 | Battery genset support enable | enum16 | Battery will support the genset in case of failure.
129 | Battery genset capacity enable | enum16 | Battery capacity backup for genset
130..131 | Battery genset capacity stop thr | FLOAT (byteorder: ABCD) | SOC stop threshold[%]
132..133 | Battery genset capacity start thr | FLOAT (byteorder: ABCD) | SOC start threshold[%]
134 | Battery grid capacity enable | enum16 | Battery capacity backup for grid
135..136 | Battery grid capacity stop thr | FLOAT (byteorder: ABCD) | SOC stop threshold[%]
137..138 | Battery grid capacity start thr | FLOAT (byteorder: ABCD) | SOC start threshold[%]
139 | Battery minimum dg load charge enable | enum16 | Charge battery when DG is below minumum dg load.
140..141 | Battery minimum dg load charge thr | FLOAT (byteorder: ABCD) | SOC stop threshold[%]
142..143 | Optimum genset load | FLOAT (byteorder: ABCD) | Optimum genset operating load in percentage
144..145 | Battery charge reference genset | FLOAT (byteorder: ABCD) | Battery charge reference from genset [%]
146..147 | Battery charge reference grid | FLOAT (byteorder: ABCD) | Battery charge reference from grid [%]
148..499 | Reserved
500..501 | Sim P load | FLOAT (byteorder: ABCD) | Simulated active load
502..503 | Sim Q load | FLOAT (byteorder: ABCD) | Simulated reactive load
504..505 | Sim F grid | FLOAT (byteorder: ABCD) | Simulated grid frequency
506..507 | Sim U grid | FLOAT (byteorder: ABCD) | Simulated grid voltage
508..509 | Sim POA | FLOAT (byteorder: ABCD) | Simulated plane of array irradiation
510..511 | Sim BOM | FLOAT (byteorder: ABCD) | Simulated back of module temperature
512 | Sim MB on | 16 unsigned int | BIT0..BIT15: Mains breaker 01..16 closed
513 | Sim GB on | 16 unsigned int | BIT0..BIT15: Genset breaker 01..16 closed
514..515 | Sim SOC | FLOAT (byteorder: ABCD) | Simulated State Of Charge
516 | Sim Grid able to close | 16 unsigned int | BIT0..BIT15: Mains breaker 01..16 able to close
517 | Sim Genset able to start | 16 unsigned int | BIT0..BIT15: Genset 01..16 able to start
518 | Sim Battery able to start | 16 unsigned int | BIT0..BIT15: Battery 01..16 able to start
519..999 | Reserved
Page02 (Commands) |  |  |  | Page02 need to be enabled
1000 | PV Start | enum16 | 0: OFF 1: ON
1001 | Genset Start | enum16 | 0: OFF 1: ON
1002 | Ack. All alarms. | enum16 | 0: OFF 1: ON | Cleared automatically by Ecpv
1003 | Ack. All alarm in line 01. | enum16 | 0: OFF 1: ON | Cleared automatically by Ecpv
1004 | Ack. All alarm in line 02. | enum16 | 0: OFF 1: ON | Cleared automatically by Ecpv
1005 | Ack. All alarm in line 03. | enum16 | 0: OFF 1: ON | Cleared automatically by Ecpv
1006 | Alarm slider | 16 signed int |  | Alarm slider control
1007 | Year | 16 unsigned int | Set ECpv RTC year
1008 | Month | 16 unsigned int | Set ECpv RTC month
1009 | Date | 16 unsigned int | Set ECpv RTC date
1010 | Hour | 16 unsigned int | Set ECpv RTC hour
1011 | Minute | 16 unsigned int | Set ECpv RTC minute
1012 | Second | 16 unsigned int | Set ECpv RTC second
1013 | Millisecond | 16 unsigned int | Set ECpv RTC millisecond
1014 | Set Ecpv RTC | enum16 | 0: OFF 1: ON | Cleared automatically by Ecpv
1015 | Battery Start | enum16 | 0: OFF 1: ON
1016 | Grid start | enum16 | 0: OFF 1: ON
1017 | Reserved
1018 | Reserved
1019 | Cmd Panel buttons 01..16 | 16 unsigned int | bitwise
1020 | ECsync Open STS | enum16 | 0: OFF 1: ON
1021 | ECsync: Ack. All alarms. | enum16 | 0: OFF 1: ON | Cleared automatically by Ecpv
1022 | REF Enables | enum16 | BIT0: PV PREF Enable (0: OFF, 1: ON) BIT1: PV QREF Enable (0: OFF, 1: ON) BIT2: BAT PREF Enable (0: OFF, 1: ON) BIT3: BAT QREF Enable (0: OFF, 1: ON) BIT4: PV COSPHIREF Enable (0: OFF, 1: ON) BIT5: BAT COSPHIREF Enable (0: OFF, 1: ON)
1023..1024 | PV PREF | FLOAT (byteorder: ABCD) | PV Active power reference setting used when grid connected [kW]
1025..1026 | PV QREF | FLOAT (byteorder: ABCD) | PV Reactive power reference setting used when grid connected [kVAr]
1027..1028 | BAT PREF | FLOAT (byteorder: ABCD) | Battery Active power reference setting used when grid connected [kW]
1029..1030 | BAT QREF | FLOAT (byteorder: ABCD) | Battery Reactive power reference setting used when grid connected [kVAr]
1031..1032 | PV COSPHIREF | FLOAT (byteorder: ABCD) | PV cosphi reference setting used when grid connected [-1;1]. | Negative being inductive and positive being capacitive
1033..1034 | BAT COSPHIREF | FLOAT (byteorder: ABCD) | Battery cosphi reference setting used when grid connected [-1;1]. | Negative being inductive and positive being capacitive
1035..1999 | Reserved
Page03 (External readings) |  |  |  | Page03 need to be enabled
2000..2001 | PV generating capacity | FLOAT (byteorder: ABCD) | PV generating panel capacity [kW] | Only used if GC compensation set to "Modbus page03".
2002..2003 | PV produced power | FLOAT (byteorder: ABCD) | The produced PV power [kW] | Only used if "Modbus page03" is selected for PV kW sensing method
2004..2005 | PV produced reactive power | FLOAT (byteorder: ABCD) | The produced PV reactive power [kVAr] | Only used if "Modbus page03" is selected for PV kW sensing method
2006..2007 | Genset generating capacity | FLOAT (byteorder: ABCD) | Gensets generating capacity connected [kW] | Only used in case "Modbus page03" is selected for GB feedback detection
2008..2009 | Genset produced power | FLOAT (byteorder: ABCD) | The total produced power of gensets connected [kW] | Only used if "Modbus page03" is selected for genset kW sensing method
2010..2011 | Genset produced reactive power | FLOAT (byteorder: ABCD) | The total produced reactive power of gensets connected [kVAr] | Only used if "Modbus page03" is selected for genset kW sensing method
2012..2013 | Grid rated capacity | FLOAT (byteorder: ABCD) | Grid rated capacity connected [kW] | Only used in case "Modbus page03" is selected for MB feedback detection
2014..2015 | Grid power | FLOAT (byteorder: ABCD) | The total grid power [kW] | Only used if "Modbus page03" is selected for mains kW sensing method
2016..2017 | Grid reactive power | FLOAT (byteorder: ABCD) | The total grid reactive power [kVAr] | Only used if "Modbus page03" is selected for mains kW sensing method
2018..2019 | Grid frequency | FLOAT (byteorder: ABCD) | The grid frequency [Hz] | Only used if "Modbus page03" is selected for mains kW sensing method
2020..2021 | Grid line-line voltage | FLOAT (byteorder: ABCD) | The grid line-line voltage [V] | Only used if "Modbus page03" is selected for mains kW sensing method
2022 | Any GB connected | 16 unsigned int | False: 0 True: 1 | Only used in case "Modbus page03" is selected for GB feedback detection
2023 | Any MB connected | 16 unsigned int | False: 0 True: 1 | Only used in case "Modbus page03" is selected for MB feedback detection
2024..2025 | POA | FLOAT (byteorder: ABCD) | POA irradiance [W/m2] | Only used in case "Modbus page03" is selected for POA Origin
2026..2027 | BOM | FLOAT (byteorder: ABCD) | Back of module temperature [C] | Only used in case "Modbus page03" is selected for BOM Origin
2028..2029 | GHI | FLOAT (byteorder: ABCD) | GHI irradiance [W/m2] | Only used in case "Modbus page03" is selected for GHI Origin
2030..2031 | Ambient temperature | FLOAT (byteorder: ABCD) | Ambient temperature [C] | Only used in case "Modbus page03" is selected for Ambient temperature Origin
2032..2033 | Wind speed | FLOAT (byteorder: ABCD) | Wind speed [m/s] | Only used in case "Modbus page03" is selected for Wind speed Origin
2034..2035 | Relative humidity | FLOAT (byteorder: ABCD) | Relative humidity [%] | Only used in case "Modbus page03" is selected for Relative humidity Origin
2036..2037 | Barometrical pressure | FLOAT (byteorder: ABCD) | Barometrical pressure [HPa] | Only used in case "Modbus page03" is selected for Barometricl pressure Origin
2038..2039 | Wind direction | FLOAT (byteorder: ABCD) | Wind direction [deg] | Only used in case "Modbus page03" is selected for Wind direction Origin
2040..2041 | Rain | FLOAT (byteorder: ABCD) | Rain fall [mm] | Only used in case "Modbus page03" is selected for Rain Origin
2042..2043 | Fuel Level 01 | FLOAT (byteorder: ABCD) | Fuel level 01 [0.1%] | Only used in case "Modbus page03" is selected for Fuel Level 01 Origin
2044..2045 | Fuel Level 02 | FLOAT (byteorder: ABCD) | Fuel level 02 [0.1%] | Only used in case "Modbus page03" is selected for Fuel level 02 Origin
2046..2047 | Fuel Level 03 | FLOAT (byteorder: ABCD) | Fuel level 03 [0.1%] | Only used in case "Modbus page03" is selected for Fuel level 03 Origin
2048..2049 | Fuel Level 04 | FLOAT (byteorder: ABCD) | Fuel level 04 [0.1%] | Only used in case "Modbus page03" is selected for Fuel level 04 Origin
2050..2999 | Reserved | FLOAT (byteorder: ABCD)
Page04 (Relay control) |  |  |  | Page04 needs to be enabled
3000 | Relay 1-16 on all DG meters | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3001 | Relay 1-16 on DG meter 1 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3002 | Relay 1-16 on DG meter 2 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3003 | Relay 1-16 on DG meter 3 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3004 | Relay 1-16 on DG meter 4 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3005 | Relay 1-16 on DG meter 5 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3006 | Relay 1-16 on DG meter 6 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3007 | Relay 1-16 on DG meter 7 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3008 | Relay 1-16 on DG meter 8 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3009 | Relay 1-16 on DG meter 9 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3010 | Relay 1-16 on DG meter 10 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3011 | Relay 1-16 on DG meter 11 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3012 | Relay 1-16 on DG meter 12 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3013 | Relay 1-16 on DG meter 13 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3014 | Relay 1-16 on DG meter 14 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3015 | Relay 1-16 on DG meter 15 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3016 | Relay 1-16 on DG meter 16 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3017 | Relay 1-16 on all PV meters | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3018 | Relay 1-16 on PV meter 1 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3019 | Relay 1-16 on PV meter 2 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3020 | Relay 1-16 on PV meter 3 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3021 | Relay 1-16 on PV meter 4 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3022 | Relay 1-16 on PV meter 5 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3023 | Relay 1-16 on PV meter 6 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3024 | Relay 1-16 on PV meter 7 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3025 | Relay 1-16 on PV meter 8 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3026 | Relay 1-16 on PV meter 9 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3027 | Relay 1-16 on PV meter 10 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3028 | Relay 1-16 on PV meter 11 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3029 | Relay 1-16 on PV meter 12 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3030 | Relay 1-16 on PV meter 13 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3031 | Relay 1-16 on PV meter 14 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3032 | Relay 1-16 on PV meter 15 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3033 | Relay 1-16 on PV meter 16 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3034 | Relay 1-16 on all Mains meters | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3035 | Relay 1-16 on Mains meter 1 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3036 | Relay 1-16 on Mains meter 2 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3037 | Relay 1-16 on Mains meter 3 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3038 | Relay 1-16 on Mains meter 4 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3039 | Relay 1-16 on Mains meter 5 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3040 | Relay 1-16 on Mains meter 6 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3041 | Relay 1-16 on Mains meter 7 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3042 | Relay 1-16 on Mains meter 8 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3043 | Relay 1-16 on Mains meter 9 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3044 | Relay 1-16 on Mains meter 10 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3045 | Relay 1-16 on Mains meter 11 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3046 | Relay 1-16 on Mains meter 12 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3047 | Relay 1-16 on Mains meter 13 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3048 | Relay 1-16 on Mains meter 14 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3049 | Relay 1-16 on Mains meter 15 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3050 | Relay 1-16 on Mains meter 16 | 16 unsigned int | bitwise | Relay enable is to be set to "ECLOGIC"
3051 | Relay 1-16 on all IO modules | 16 unsigned int | bitwise
3052 | Relay 1-16 on IO module 1 | 16 unsigned int | bitwise
3053 | Relay 1-16 on IO module 2 | 16 unsigned int | bitwise
3054 | Relay 1-16 on IO module 3 | 16 unsigned int | bitwise
3055 | Relay 1-16 on IO module 4 | 16 unsigned int | bitwise
3056 | EClogic Modbus Event 01-16 | 16 unsigned int | bitwise | Maps to input register page for use in Eclogic
3057 | EClogic Modbus Event 17-32 | 16 unsigned int | bitwise | Maps to input register page for use in Eclogic
3056..3999 | Reserved
Page05 (DNP3 control) |  |  |  | Page05 needs to be enabled
4000..4001 | PV active Power [W] | FLOAT (byteorder: ABCD) | PV active power generated in Watts
4002..4003 | PV reactive Power [VAr] | FLOAT (byteorder: ABCD) | PV reactive power generated in Vars
4004..4005 | Mains active Power [W] | FLOAT (byteorder: ABCD) | Active power import/export from the grid in Watts
4006..4007 | Power reference [%] | FLOAT (byteorder: ABCD) | Active PV power reference in percentage (read)
4008..4009 | Power ramp up rate [%/min] | FLOAT (byteorder: ABCD) | Active PV power ramp up rate in %/min (read)
4010..4011 | Power ramp down rate [%/min] | FLOAT (byteorder: ABCD) | Active PV power ramp down rate in %/min (read)
4012 | Power reference [%] | 16 signed int | Active PV power reference in percentage (write)
4013 | Power ramp up rate [%/min] | 16 signed int | Active PV power ramp up rate in %/min (write)
4014 | Power ramp down rate [%/min] | 16 signed int | Active PV power ramp down rate in %/min (write)
4015..4999 | Reserved
ECgrid Area |  |  |  | ECgrid Slave needs to be enabled
READ
6000..6005 | ECpvX MAC | string | Mac addres of the ECpvX (12 chars)
6006..6007 | Rated BESS power | FLOAT (byteorder: ABCD) | Rated power of the BESS [kW]
6008..6009 | Rated BESS hours | FLOAT (byteorder: ABCD) | Rated hours of the BESS [h]
6010..6011 | BESS Power | FLOAT (byte order: ABCD) | BESS power procution [kW]
6012..6013 | BESS SOC | FLOAT (byte order: ABCD) | Battery State Of Charge [%]
6014 | Bat Started | enum16 | 0: Battery stopped 1: Battery started
6015..6099 | Reserved
WRITE
6100 | WD Counter | 16 unsigned int | WD Counter to signal ECgrid is alive
6101 | Freq service status | enum16 | 0: Frequency service inactive 1: Frequency service active
6102 | Freq service area | enum16 | 0: Central europe sync. area 1: Nordic sync. area
6103..6104 | Freq service cap | FLOAT (byte order: ABCD) | Frequency service capacity [kW]
6105 | ECgrid status | enum16 | 0: Mains meter missing 1: Freq service schedule read alarm 2: Frequency service schdule valid AND Nordic sync. area selected 3: Frequency service schdule valid AND Central Europe sync. area selected
6106..6107 | Freq service power reference | FLOAT (byteorder: ABCD) | BESS power reference from frequency services [kW]
6108 | SOC Management status | enum16 | 0: Inactive 1: Active
6109..6110 | SOC Management power reference | FLOAT (byteorder: ABCD) | BESS power reference from SOC Management [kW]
6111..6199 | Reserved
ECev Area
READ
8000..8001 | PV_P_GENERATING_CAPACITY | FLOAT (byte order: ABCD) | Total PV generating capacity active power [kW]
8002..8003 | DG_P_GENERATING_CAPACITY | FLOAT (byte order: ABCD) | Total genset generating capacity active power [kW]
8004..8005 | MAINS_P_GENERATING_CAPACITY | FLOAT (byte order: ABCD) | Total Mains generating capacity active power [kW]
8006..8007 | BATTERY_P_GENERATING_CAPACITY | FLOAT (byte order: ABCD) | Total Battery inverter generating capacity active power [kW]
8008..8009 | POWER_P_PV_TOTAL | FLOAT (byte order: ABCD) | Total PV active power [kW]
8010..8011 | POWER_P_DG_TOTAL | FLOAT (byte order: ABCD) | Total genset active power [kW]
8012..8013 | POWER_P_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total Mains active power [kW]
8014..8015 | POWER_P_BAT_TOTAL | FLOAT (byte order: ABCD) | Total battery active power [kW]
8016..8017 | POWER_Q_PV_TOTAL | FLOAT (byte order: ABCD) | Total PV reactive power [kVAr]
8018..8019 | POWER_Q_DG_TOTAL | FLOAT (byte order: ABCD) | Total genset reactive power [kVAr]
8020..8021 | POWER_Q_MAINS_TOTAL | FLOAT (byte order: ABCD) | Total mains reactive power [kVAr]
8022..8023 | POWER_Q_BAT_TOTAL | FLOAT (byte order: ABCD) | Total battery reactive power [kVAr]
8024..8025 | BATTERY_SOC_PCT | FLOAT (byte order: ABCD) | Battery State Of Charge [%]
8026..8027 | BATTERY_SOH_PCT | FLOAT (byte order: ABCD) | Battery State Of Health [%]
8028..8029 | BATTERY_SOE_KWH | FLOAT (byte order: ABCD) | Battery State Of Energy [kWh]
8030..8031 | BATTERY_ODC_KW | FLOAT (byte order: ABCD) | Battery online discharge capacity [kW]
8032..8033 | BATTERY_OCC_KW | FLOAT (byte order: ABCD) | Battery online charge capacity [kW]
8034..8039 | ECpvX MAC | string | Mac addres of the ECpvX (12 chars)
8040..8041 | BAT_STOP_ALL_CHARGING | FLOAT (byte order: ABCD) | Battery charging upper SOC limit [%]
8042..8043 | BAT_STOP_ALL_DISCHARGING | FLOAT (byte order: ABCD) | Battery discharging lower SOC limit [%]
8044..8045 | BAT_CHARGE_DG_START_SOC | FLOAT (byte order: ABCD) | Genset charging lower SOC limit [%]
8046..8047 | BAT_CHARGE_DG_STOP_SOC | FLOAT (byte order: ABCD) | Genset charging upper SOC limit [%]
8048..8049 | BAT_CHARGE_MAINS_START_SOC | FLOAT (byte order: ABCD) | Mains charging lower SOC limit [%]
8050..8051 | BAT_CHARGE_MAINS_STOP_SOC | FLOAT (byte order: ABCD) | Mains charging upper SOC limit [%]
8052..8053 | BAT_CHARGE_PV_START_SOC | FLOAT (byte order: ABCD) | PV charging lower SOC limit [%]
8054..8055 | BAT_CHARGE_PV_STOP_SOC | FLOAT (byte order: ABCD) | PV charging upper SOC limit [%]
8056 | BAT_CHARGE_DG_ENA | 16 unsigned int | 0: DISABLED 1: ENABLED
8057 | BAT_CHARGE_MAINS_ENA | 16 unsigned int | 0: DISABLED 1: ENABLED
8058 | BAT_CHARGE_PV_ENA | 16 unsigned int | 0: DISABLED 1: ENABLED
8059 | MAINS_P_CTRL_MODE | 16 unsigned int | 0: MAINS_P_FIXED 1: MAINS_P_FIXED_PCC
8060 | MAINS_BAT_P_CTRL_MODE | 16 unsigned int | 0: MAINS_BAT_P_SYSTEM 1: MAINS_BAT_P_FIXED 2: MAINS_BAT_P_SA 3: MAINS_BAT_P_PCC_SA
8061 | MAINS_Q_CTRL_MODE | 16 unsigned int | 0: MAINS_Q_FIXED 1: MAINS_Q_FIXED_PCC 2: MAINS_COSPHI_C_FIXED 3: MAINS_COSPHI_C_FIXED_PCC 4: MAINS_COSPHI_I_FIXED 5: MAINS_COSPHI_I_FIXED_PCC 6: MAINS_SHARE_PF
8062 | MAINS_BAT_Q_CTRL_MODE | 16 unsigned int | 0: MAINS_BAT_Q_SYSTEM 1: MAINS_BAT_Q_FIXED 2: MAINS_BAT_COSPHI_C_FIXED 3: MAINS_BAT_COSPHI_I_FIXED
8063 | ECEV_EVT1 | 16 unsigned int | bitwise
8064 | ECEV_EVT2 | 16 unsigned int | bitwise
8065 | ECEV_EVT3 | 16 unsigned int | bitwise
8066 | ECEV_EVT4 | 16 unsigned int | bitwise
8067..8068 | ECEV_BAT_BATTERY_P | FLOAT (byte order: ABCD) | Battery Rated Active Power [kW]
8069..8070 | POWER_P_DCPV_TOTAL | FLOAT (byte order: ABCD) | Total DCPV power [kW]
WRITE
8100 | ECEV_ENABLE | 16 unsigned int | bitwise
8101 | ANY_EV_LOAD_ACTIVE | 16 unsigned int | bitwise
SunSpec profile
Address | DataLabel | DataType | Description | Supported
40000..40001 | SID | 32 unsigned int | A well-known value 0x53756e53. Uniquely identifies this as a SunSpec Modbus Map | x
40002 | ID | 16 unsigned int | A well-known value 1. Uniquely identifies this as a SunSpec Common Model | x
40003 | L | 16 unsigned int | Well-known # of 16 bit registers to follow : 66 | x
40004..40019 | Manufacturer | string | Manufacturer specific value (32 chars) | x
40020..40035 | Model | string | Manufacturer specific value (32 chars) | x
40036..40043 | Options | string | Manufacturer specific value (16 chars)
40044..40051 | Version | string | Manufacturer specific value (16 chars) | x
40052..40067 | Serial Number | string | Manufacturer specific value (32 chars) | x
40068 | Device Address | 16 unsigned int | Modbus device address
40069 | Pad | 16 unsigned int | Force even alignment
40070 | ID | 16 unsigned int | A well-known value 113. Uniquely identifies this as a SunSpec Inverter (Three Phase) FLOAT Model | x
40071 | L | 16 unsigned int | Well-known # of 16 bit registers to follow : 60 | x
40072..40073 | Amps | FLOAT (byteorder: ABCD) | AC Current
40074..40075 | Amps PhaseA | FLOAT (byteorder: ABCD) | Phase A Current
40076..40077 | Amps PhaseB | FLOAT (byteorder: ABCD) | Phase B Current
40078..40079 | Amps PhaseC | FLOAT (byteorder: ABCD) | Phase C Current
40080..40081 | Phase Voltage AB | FLOAT (byteorder: ABCD) | Phase Voltage AB
40082..40083 | Phase Voltage BC | FLOAT (byteorder: ABCD) | Phase Voltage BC
40084..40085 | Phase Voltage CA | FLOAT (byteorder: ABCD) | Phase Voltage CA
40086..40087 | Phase Voltage AN | FLOAT (byteorder: ABCD) | Phase Voltage AN
40088..40089 | Phase Voltage BN | FLOAT (byteorder: ABCD) | Phase Voltage BN
40090..40091 | Phase Voltage CN | FLOAT (byteorder: ABCD) | Phase Voltage CN
40092..40093 | Watts | FLOAT (byteorder: ABCD) | AC Power | x
40094..40095 | Hz | FLOAT (byteorder: ABCD) | Line Frequency
40096..40097 | VA | FLOAT (byteorder: ABCD) | AC Apparent Power | x
40098..40099 | VAr | FLOAT (byteorder: ABCD) | AC Reactive Power | x
40100..4010 | PF | FLOAT (byteorder: ABCD) | AC Power Factor | x
40102..40103 | WattHours | FLOAT (byteorder: ABCD) | AC Energy | x
40104..40105 | DC Amps | FLOAT (byteorder: ABCD) | DC Current
40106..40107 | DC Voltage | FLOAT (byteorder: ABCD) | DC Voltage
40108..40109 | DC Watts | FLOAT (byteorder: ABCD) | DC Power
40110..40111 | Cabinet Temperature | FLOAT (byteorder: ABCD) | Cabinet Temperature
40112..40113 | Heat Sink Temperature | FLOAT (byteorder: ABCD) | Heat Sink Temperature
40114..40115 | Transformer Temperature | FLOAT (byteorder: ABCD) | Transformer Temperature
40116..40117 | Other Temperature | FLOAT (byteorder: ABCD) | Other Temperature
40118 | Operating State | enum16 | Enumerated value. Operating state
40119 | Vendor Operating State | enum16 | Vendor specific operating state code
40120..40121 | Event1 | bitfield32 | Bitmask value. Event fields
40122..40123 | Event Bitfield 2 | bitfield32 | Reserved for future use
40124..40125 | Vendor Event Bitfield 1 | bitfield32 | Vendor defined events
40126..40127 | Vendor Event Bitfield 2 | bitfield32 | Vendor defined events
40128..40129 | Vendor Event Bitfield 3 | bitfield32 | Vendor defined events
40130..40131 | Vendor Event Bitfield 4 | bitfield32 | Vendor defined events
40132 | ID | 16 unsigned int | A well-known value 121. Uniquely identifies this as a SunSpec Basic Settings Model | x
40133 | L | 16 unsigned int | Well-known # of 16 bit registers to follow : 30 | x
40134 | WMax | 16 unsigned int | Setting for maximum power output. Default to WRtg. | x
40135 | VRef | 16 unsigned int | Voltage at the PCC.
40136 | VRefOfs | 16 signed int | Offset from PCC to inverter.
40137 | VMax | 16 unsigned int | Setpoint for maximum voltage.
40138 | VMin | 16 unsigned int | Setpoint for minimum voltage.
40139 | VAMax | 16 unsigned int | Setpoint for maximum apparent power. Default to VARtg. | x
40140 | VArMaxQ1 | 16 signed int | Setting for maximum reactive power in quadrant 1. Default to VArRtgQ1. | x
40141 | VArMaxQ2 | 16 signed int | Setting for maximum reactive power in quadrant 2. Default to VArRtgQ2. | x
40142 | VArMaxQ3 | 16 signed int | Setting for maximum reactive power in quadrant 3. Default to VArRtgQ3. | x
40143 | VArMaxQ4 | 16 signed int | Setting for maximum reactive power in quadrant 4. Default to VArRtgQ4. | x
40144 | WGra | 16 unsigned int | Default ramp rate of change of active power due to command or internal action.
40145 | PFMinQ1 | 16 signed int | Setpoint for minimum power factor value in quadrant 1. Default to PFRtgQ1.
40146 | PFMinQ2 | 16 signed int | Setpoint for minimum power factor value in quadrant 2. Default to PFRtgQ2.
40147 | PFMinQ3 | 16 signed int | Setpoint for minimum power factor value in quadrant 3. Default to PFRtgQ3.
40148 | PFMinQ4 | 16 signed int | Setpoint for minimum power factor value in quadrant 4. Default to PFRtgQ4.
40149 | VArAct | enum16 | VAR action on change between charging and discharging: 1=switch 2=maintain VAR characterization.
40150 | ClcTotVA | enum16 | Calculation method for total apparent power. 1=vector 2=arithmetic.
40151 | MaxRmpRte | 16 unsigned int | Setpoint for maximum ramp rate as percentage of nominal maximum ramp rate. This setting will limit the rate that watts delivery to the grid can increase or decrease in response to intermittent PV generation.
40152 | ECPNomHz | 16 unsigned int | Setpoint for nominal frequency at the ECP.
40153 | ConnPh | enum16 | Identity of connected phase for single phase inverters. A=1 B=2 C=3.
40154 | WMax_SF | sunssf | Scale factor for real power. | x
40155 | VRef_SF | sunssf | Scale factor for voltage at the PCC.
40156 | VRefOfs_SF | sunssf | Scale factor for offset voltage.
40157 | VMinMax_SF | sunssf | Scale factor for min/max voltages.
40158 | VAMax_SF | sunssf | Scale factor for apparent power. | x
40159 | VArMax_SF | sunssf | Scale factor for reactive power. | x
40160 | WGra_SF | sunssf | Scale factor for default ramp rate.
40161 | PFMin_SF | sunssf | Scale factor for minimum power factor.
40162 | MaxRmpRte_SF | sunssf | Scale factor for maximum ramp percentage.
40163 | ECPNomHz_SF | sunssf | Scale factor for nominal frequency.
40164 | ID | 16 unsigned int | A well-known value 123. Uniquely identifies this as a SunSpec Immediate Controls Model | x
40165 | L | 16 unsigned int | Well-known # of 16 bit registers to follow : 24 | x
40166 | Conn_WinTms | 16 unsigned int | Time window for connect/disconnect.
40167 | Conn_RvrtTms | 16 unsigned int | Timeout period for connect/disconnect.
40168 | Conn | enum16 | Enumerated valued. Connection control.
40169 | WMaxLimPct | 16 unsigned int | Set power output to specified level. | x
40170 | WMaxLimPct_WinTms | 16 unsigned int | Time window for power limit change.
40171 | WMaxLimPct_RvrtTms | 16 unsigned int | Timeout period for power limit.
40172 | WMaxLimPct_RmpTms | 16 unsigned int | Ramp time for moving from current setpoint to new setpoint.
40173 | WMaxLim_Ena | enum16 | Enumerated valued. Throttle enable/disable control. | x
40174 | OutPFSet | 16 signed int | Set power factor to specific value - cosine of angle.
40175 | OutPFSet_WinTms | 16 unsigned int | Time window for power factor change.
40176 | OutPFSet_RvrtTms | 16 unsigned int | Timeout period for power factor.
40177 | OutPFSet_RmpTms | 16 unsigned int | Ramp time for moving from current setpoint to new setpoint.
40178 | OutPFSet_Ena | enum16 | Enumerated valued. Fixed power factor enable/disable control.
40179 | VArWMaxPct | 16 signed int | Reactive power in percent of WMax.
40180 | VArMaxPct | 16 signed int | Reactive power in percent of VArMax. | x
40181 | VArAvalPct | 16 signed int | Reactive power in percent of VArAval.
40182 | VArPct_WinTms | 16 unsigned int | Time window for VAR limit change.
40183 | VArPct_RvrtTms | 16 unsigned int | Timeout period for VAR limit.
40184 | VArPct_RmpTms | 16 unsigned int | Ramp time for moving from current setpoint to new setpoint.
40185 | VArPct_Mod | enum16 | Enumerated value. VAR percent limit mode. | x (2)
40186 | VArPct_Ena | enum16 | Enumerated valued. Percent limit VAr enable/disable control. | x
40187 | WMaxLimPct_SF | sunssf | Scale factor for power output percent. | x (-2)
40188 | OutPFSet_SF | sunssf | Scale factor for power factor.
40189 | VArPct_SF | sunssf | Scale factor for reactive power percent. | x (-2)
40190 | ID | 16 unsigned int | A well-known value 0xFFFF. Uniquely identifies this as a SunSpec End Model | x

## Coils 0x01
Proprietary profile
Address | DataLabel | DataType | Description | Note
Page05 (DNP3 control) |  |  |  | Page05 needs to be enabled
4000 | PV Ctrl. Active | Boolean | Superior power control from DNP3 (page05) active
4001 | PV Ramp Ctrl. Active | Boolean | Superior power ramp control from DNP3 (page05) active
4002..4999 | Reserved